## Sheet1
Device label | Model | Serial number | NMC Firmware version | IP Address | Location | UPS Score | UPS from YYYY-MM | Battery from YYYY-MM | Battery Temperature (avg 24h deg C) | Internal Battery Sku number | Load (average 30 days in %) | Load (max 30 days in %) | Recommendation | Projected health | Projected health at optimal temperature
apc854FE1 | Smart-UPS 2200 | AS1430142069 | v7.1.2 | 10.46.112.110 | RBG Santa Fe Springs | 5.09 | 2014-07 | 2014-07 | 31.21 | RBC43 | 18.11 | 20.9 | Replace battery, Lower the battery temperature to 25 degrees C
apcBA00C2 | Smart-UPS 2200 | AS1430142070 | v7.1.2 | 10.46.112.105 | RBG Santa Fe Springs | 6.34 | 2014-07 | 2018-12 | 29.01 | RBC43 | 0 | 0 | Replace battery, Lower the battery temperature to 25 degrees C
RCCB-RANCHO-UPS1 | Smart-UPS X 3000 | AS1425145718 | v6.5.6 | 10.48.115.228 | RCCB Rancho | 6.35 | 2014-06 | 2015-11 | 29.21 | APCRBC117 | 9.52 | 10.9 | Replace battery, Lower the battery temperature to 25 degrees C
MBUS-StJohns-MDF-UPS3 | Smart-UPS X 3000 | AS1718163853 | v6.5.6 | 10.20.52.229 | MBUS St Johns | 9.84 | 2017-05 | 2020-09 | 33.33 | APCRBC117 | 4.89 | 5.4 | Lower the battery temperature to 25 degrees C
GLCCD-EAGAN-UPS-SW4 | Smart-UPS 750 | AS1829144771 | v7.1.2 | 10.20.206.16 | GLCCD Eagan | 11.07 | 2018-07 | 2018-11 | 35.43 | RBC123 | 56.82 | 57.9 | Replace battery, Lower the battery temperature to 25 degrees C
RCCB-BAKERSFIELD-UPS-SW3-Guard | Smart-UPS 1000 | 3S1846X17590 | v6.6.4 | 10.47.18.103 | RCCB Bakersfield | 11.55 | 2018-11 | 2019-02 | 32.28 | APCRBC132 | 13.7 | 14.1 | Replace battery, Lower the battery temperature to 25 degrees C
MBUS-Dickson-IDF1-UPS1 | Smart-UPS 1000 | 3S1831X15296 | v6.5.0 | 172.16.16.103 | MBUS Dickson | 12.33 | 2018-08 | 2018-11 | 31.32 | APCRBC132 | 33.57 | 35 | Replace battery, Lower the battery temperature to 25 degrees C
apc33387A | Smart-UPS SRT 1500 | AS2016190961 | v7.1.2 | 10.53.178.69 | RBG Monterey | 12.67 | 2020-04 | 2020-04 | 29.11 | APCRBC155 | 41 | 42.7 | Lower the battery temperature to 25 degrees C
RCCB-Eureka-UPS1 | Smart-UPS X 1500 | AQ1625130524 | v6.5.0 | 10.47.146.228 | RCCB Eureka | 13.89 | 2016-06 | 2019-02 | 31.11 | APCRBC115 | 15.1 | 15.5 | Replace battery, Lower the battery temperature to 25 degrees C
apc266CC0 | Smart-UPS 750 | AS1936145175 | v7.1.2 | 10.52.98.51 | RBG Lancaster | 15.55 | 2019-09 | 2019-09 | 33.98 | RBC123 | 50.7 | 57.9 | Lower the battery temperature to 25 degrees C
apc267176 | Smart-UPS 750 | AS1936145181 | v7.1.2 | 10.52.98.50 | RBG Lancaster | 15.87 | 2019-09 | 2019-09 | 33.77 | RBC123 | 60.26 | 63.8 | Lower the battery temperature to 25 degrees C
RBGSummervilleAPC1 | Smart-UPS 1500 | AS1426114643 | v7.1.2 | 10.20.100.228 | RBG Summerville | 16.15 | 2014-06 | 2014-06 | 29.57 | RBC7 | 30.59 | 32.6 | Replace battery, Lower the battery temperature to 25 degrees C
GLCCD-AlsipDC-UPS-SW2-WH-CENTRAL | Smart-UPS 750 | AS2102143526 | v1.3.3.1 | 10.20.145.234 | GLCCD Alsip | 16.87 | 2021-01 | 2021-01 | 36.93 | RBC123 | 38.3 | 42.9 | Lower the battery temperature to 25 degrees C
apc4F07F2 | Smart-UPS SRT 1500 | AS1942291101 | v7.1.2 | 10.52.226.65 | RBG Imperial | 16.91 | 2019-10 | 2019-10 | 25.56 | APCRBC155 | 21.09 | 21.9 | Lower the battery temperature to 25 degrees C
GLCCD-EAGAN-UPS-SERV-S15 | Smart-UPS X 3000 | AS1908265339 | v7.1.2 | 10.20.207.98 | GLCCD Eagan | 17.09 | 2019-02 | 2019-02 | 30.63 | APCRBC117 | 6.87 | 7.9 | Replace battery, Lower the battery temperature to 25 degrees C
RCCB-RANCHO-UPS2 | Smart-UPS X 3000 | AS1425145722 | v6.5.6 | 10.48.115.229 | RCCB Rancho | 17.63 | 2014-06 | 2015-11 | 26.78 | APCRBC117 | 14.03 | 16.8 | Replace battery, Lower the battery temperature to 25 degrees C
apc4D63B8 | Smart-UPS 750 | 3S1912X11096 | v7.1.2 | 10.51.98.159 | RBG Chico | 18.78 | 2019-03 | 2019-06 | 28.92 | APCRBC48 | 46.68 | 57.8 | Lower the battery temperature to 25 degrees C | 2024-06-19 | 2024-06-21
RH Office 10S Switches | Smart-UPS 2200 | IS1147003100 | v6.2.1 | 10.20.7.11 | RH Rosemont 10th Floor | 20.16 | 2011-11 | 2022-08 | 24.48 | RBC43 | 29.18 | 30.5 | Replace UPS, Lower the battery temperature to 25 degrees C | 2026-02-22 | 2026-03-15
RBG-Huntington-Beach-UPS1 | Smart-UPS SRT 1500 | AS2016190969 | v6.8.2 | 10.28.92.23 | RBG Huntington Beach | 22.69 | 2020-04 | 2020-04 | 23.74 | APCRBC155 | 16.92 | 17.7
apc589F8E | Smart-UPS 750 | AS2135261745 | v1.3.3.1 | 10.20.44.151 | RBG Doral | 22.99 | 2021-09 | 2021-09 | 33.24 | RBC123 | 39.69 | 40.9 | Lower the battery temperature to 25 degrees C
RCCB-SantaMaria-UPS | Smart-UPS 2200 | AS1920161457 | v6.6.4 | 10.48.211.182 | RCCB Santa Maria | 23.6 | 2019-05 | 2019-05 | 19.99 | RBC43 | 15.21 | 16.9 | Replace battery
MBUS-StJohns-MDF-UPS1 | Smart-UPS SRT 1500 | AS2122293187 | v1.3.3.1 | 10.52.208.23 | MBUS St Johns | 23.84 | 2021-06 | 2021-06 | 31.94 | APCRBC155 | 65.82 | 84.6 | Lower the battery temperature to 25 degrees C
GLCCD-GrandRapids-UPS-SD1 | Smart-UPS SRT 1500 | AS2115192982 | v1.3.3.1 | 10.45.192.23 | GLCCD Grand Rapids | 23.93 | 2021-04 | 2021-04 | 41.94 | APCRBC155 | 88.04 | 117.6 | Lower the battery temperature to 25 degrees C | 2025-08-15 | 2025-10-31
GLCCD-VanBuren-UPS-SD1 | Smart-UPS SRT 1500 | AS2032292987 | v7.1.2 | 10.44.208.23 | GLCCD Van Buren | 25.09 | 2020-08 | 2020-08 | 27.65 | APCRBC155 | 60.94 | 62.7 | Lower the battery temperature to 25 degrees C
GLCCD-Clarkesville-UPS | Smart-UPS 750 | AS2123141730 | v1.3.3.1 | 10.53.34.246 | GLCCD Clarksville | 25.46 | 2021-06 | 2021-06 | 35.92 | RBC123 | 36.16 | 38.3 | Lower the battery temperature to 25 degrees C
apc20F3C8 | Smart-UPS 750 | AS1915232548 | v7.1.2 | 10.20.33.192 | RBG Chesapeake-VA | 25.56 | 2019-04 | 2019-04 | 24.19 | RBC123 | 55.97 | 57.2 | Replace battery
apc296849 | Smart-UPS 750 | AS1948231393 | v7.1.2 | 10.52.226.203 | RBG Imperial | 25.56 | 2019-11 | 2019-11 | 7.44 | RBC123 | 18.18 | 18.9 |  | 2024-08-23 | 2024-08-23
apc0E5110 | Smart-UPS 750 | AS1828131643 | v7.1.2 | 10.46.146.157 | RBG Richmond-VA | 25.62 | 2018-07 | 2018-07 | 27.04 | RBC123 | 41.69 | 43 | Replace battery, Lower the battery temperature to 25 degrees C
MBUS-Garner-XXX-UPS3 | Smart-UPS 1000 | 3S1832X18897 | v6.5.0 | 10.50.42.61 | MBUS Garner | 26.68 | 2018-08 | 2023-04 | 38.35 | APCRBC132 | 74.46 | 78.2 | Lower the battery temperature to 25 degrees C | 2025-05-12 | 2026-11-01
apc6FE9FB | Smart-UPS SRT 1500 | AS2218291860 | v2.0.0.6 | 10.56.10.144 | RBG Kauai | 27.36 | 2022-05 | 2022-05 | 38.54 | APCRBC155 | 6.32 | 6.9 | Lower the battery temperature to 25 degrees C
RBD-San-Bernardino-UPS1 | Smart-UPS SRT 1500 | AS2111290792 | v1.3.3.1 | 10.28.60.23 | RBG San Bernardino | 27.43 | 2021-03 | 2021-03 | 25.23 | APCRBC155 | 41.87 | 46 | Lower the battery temperature to 25 degrees C | 2026-04-10 | 2026-05-14
apc6FCF0D | Smart-UPS SRT 1500 | AS2218291861 | v2.0.0.6 | 10.56.10.58 | RBG Kauai | 27.81 | 2022-05 | 2022-05 | 34.54 | APCRBC155 | 6.64 | 6.9 | Lower the battery temperature to 25 degrees C
apc23301C | Smart-UPS 750 | AS1924131695 | v7.1.2 | 10.51.128.95 | RBG West Sacramento | 28.66 | 2019-06 | 2019-06 | 31.49 | RBC123 | 53.93 | 60.4 | Lower the battery temperature to 25 degrees C | 2025-01-13 | 2025-02-07
GLCCD-HighlandPark-UPS-SD2 | Smart-UPS SRT 1500 | AS2128290915 | v1.3.3.1 | 10.44.192.24 | GLCCD Highland Park | 29.42 | 2021-07 | 2021-07 | 29.39 | APCRBC155 | 53.14 | 57.9 | Lower the battery temperature to 25 degrees C | 2024-09-14 | 2024-10-30
GLCCD-HighlandPark-UPS | Smart-UPS 3000 | AS2112261823 | v1.3.3.1 | 10.44.192.118 | GLCCD Highland Park | 30.28 | 2021-03 | 2021-03 | 28.48 | RBC43 | 6.98 | 7.1 | Lower the battery temperature to 25 degrees C | 2025-01-14 | 2025-04-19
GLCCD-FLINT-UPS-MDF | Smart-UPS 3000 | AS2110155191 | v1.3.3.1 | 10.44.163.228 | GLCCD Flint | 30.3 | 2021-03 | 2021-03 | 27.56 | RBC43 | 19.84 | 20.8 | Lower the battery temperature to 25 degrees C | 2025-01-02 | 2025-03-12
apcB6D7A7 | Smart-UPS 2200 | AS1348244033 | v6.0.6 | 10.20.128.156 | MBCAN Brampton | 31.37 | 2013-11 | 2013-11 | 19.03 | RBC43 | 15.49 | 16.9 | Replace UPS, Replace battery
MBUS-Dickson-IDF2-UPS | Smart-UPS X 1500 | AS2046234801 | v1.1.0.16 | 172.16.16.96 | MBUS Dickson | 31.53 | 2020-11 | 2020-11 | 28.27 | APCRBC115 | 16.87 | 17.4 | Lower the battery temperature to 25 degrees C | 2025-06-06 | 2025-09-14
RBD-Doral-UPS2 | Smart-UPS SRT 1500 | AS2108195647 | v1.3.3.1 | 10.28.44.24 | RBG Doral | 31.71 | 2021-02 | 2021-02 | 24.03 | APCRBC155 | 0 | 0 |  | 2026-10-28 | 2026-11-02
MBUS-Coatsville-MDF-UPS4 | Smart-UPS X 3000 | AS1822152656 | v6.5.0 | 10.20.54.89 | MBUS Coatesville | 31.98 | 2018-05 | 2018-05 | 24.81 | APCRBC117 | 22.05 | 24.3 | Replace battery
apc75B601 | Smart-UPS X 3000 | AS2240154601 | v2.0.0.6 | 172.16.233.130 | RH Rosemont 9th Floor | 32.03 | 2022-10 | 2022-10 | 29.03 | APCRBC143 | 21.45 | 23 | Lower the battery temperature to 25 degrees C | 2026-05-06 | 2027-06-24
MBUS-StJohns-MDF-UPS2 | Smart-UPS SRT 1500 | AS2122293194 | v1.3.3.1 | 10.52.208.24 | MBUS St Johns | 32.28 | 2021-06 | 2021-06 | 28.94 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2025-01-24 | 2025-03-29
apcB6D7A6 | Smart-UPS 2200 | AS1346243783 | v6.0.6 | 192.168.40.126 | MBCAN Montreal | 32.41 | 2013-11 | 2013-11 | 18.52 | RBC43 | 0 | 0 | Replace UPS, Replace battery
RH Office 8S Switches | Smart-UPS X 3000 | AQ1415134243 | v5.1.3 | 172.16.232.222 | RH Rosemont 8th Floor | 33.06 | 2016-01 | 2022-09 | 28.2 |  | 18.74 | 20.5 | Lower the battery temperature to 25 degrees C | 2026-08-27 | 2027-08-26
RCCB-CityOfIndustry-UPS | Smart-UPS X 3000 | AS1824254616 | v6.5.0 | 10.47.83.228 | RCCB City of Industry | 33.08 | 2018-06 | 2020-12 | 20.72 | APCRBC117 | 40.8 | 42 |  | 2026-09-02 | 2026-09-02
MBUS-CID-XXXX-UPS-4 | Smart-UPS 1500 | AS1903332295 | v6.5.6 | 10.50.138.60 | MBUS City of Industry | 33.41 | 2019-01 | 2019-07 | 19.93 | APCRBC133 | 23.15 | 25.3 |  | 2024-08-07 | 2024-08-07
MBUS-McCook-MDF-UPS3 | Smart-UPS SRT 5000 | AS2234273145 | v2.0.0.6 | 10.50.10.153 | MBUS McCook | 33.59 | 2022-08 | 2016-12 | 27 | APCRBC140 | 37.49 | 43.3 | Replace battery, Lower the battery temperature to 25 degrees C
apc0E7187 | Smart-UPS 750 | AS1828140963 | v7.1.2 | 10.46.114.68 | RBG Santa Fe Springs | 33.89 | 2018-07 | 2018-07 | 27.11 | RBC123 | 28.01 | 29.2 | Replace battery, Lower the battery temperature to 25 degrees C
Unknown | Smart-UPS X 3000 | IS1252000036 | v5.1.7 | 10.48.19.166 | RCCB Salinas | 34.62 | 2012-12 | 2017-12 | 20.31 |  | 0.11 | 1.8 | Replace UPS, Replace battery
MBUS-Manassas-UPS2 | Smart-UPS SRT 1500 | AS2040195000 | v6.8.2 | 10.50.240.24 | MBUS Manassas | 34.7 | 2020-10 | 2020-10 | 23.53 | APCRBC155 | 31.53 | 34.6 |  | 2025-03-10 | 2025-03-14
RCCB-Sacramento-SW8-9-WH | Smart-UPS X 1500 | AS1815234277 | v6.5.0 | 10.47.178.228 | RCCB Sacramento | 34.77 | 2018-04 | 2018-04 | 25.63 | APCRBC115 | 0.09 | 3.2 | Replace battery, Lower the battery temperature to 25 degrees C
GLCCD-Caledonia-MDF-UPS3 | Smart-UPS X 1500 | AS2046234774 | v1.1.0.16 | 10.58.10.13 | GLCCD Caledonia | 34.88 | 2020-11 | 2020-11 | 24.49 | APCRBC115 | 40.72 | 41.8 |  | 2026-06-19 | 2026-06-19
GLCCD-HighlandPark-UPS-SD1 | Smart-UPS SRT 1500 | AS2128290913 | v1.3.3.1 | 10.44.192.23 | GLCCD Highland Park | 35.22 | 2021-07 | 2021-07 | 27.96 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2025-01-31 | 2025-04-15
MBUS-Manassas-UPS1 | Smart-UPS SRT 1500 | AS2032292983 | v6.8.2 | 10.50.240.23 | MBUS Manassas | 35.57 | 2020-08 | 2020-08 | 23.96 | APCRBC155 | 41.54 | 50.2 |  | 2025-12-21 | 2026-01-16
MBUS-Conroe-MDF-UPS1 | Smart-UPS SRT 1500 | AS2123190211 | v1.3.3.1 | 10.50.176.126 | MBUS Conroe | 35.64 | 2021-06 | 2021-06 | 28.26 | APCRBC155 | 16.95 | 17.8 | Lower the battery temperature to 25 degrees C | 2025-05-06 | 2025-07-06
GLCCD-MARQUETTE-UPS | Smart-UPS 1500 | AS2046233147 | v1.1.0.16 | 10.20.220.153 | GLCCD Marquette | 35.98 | 2020-11 | 2020-11 | 28.02 | APCRBC133 | 20.1 | 20.8 | Lower the battery temperature to 25 degrees C
apc0E5A67 | Smart-UPS 750 | AS1828131641 | v7.1.2 | 10.46.146.244 | RBG Richmond-VA | 36.1 | 2018-07 | 2018-07 | 26.25 | RBC123 | 18.9 | 19.6 | Replace battery, Lower the battery temperature to 25 degrees C
apc9A3660 | Smart-UPS 1500 | AS1412134068 | v7.1.2 | 192.168.70.220 | MBCAN Calgary | 36.62 | 2014-03 | 2014-03 | 15.55 | APCRBC133 | 19.43 | 20.1 | Replace UPS, Replace battery
MBUS-Orlando-MDF-UPS1 | Smart-UPS SRT 1500 | AS2032292981 | v6.8.2 | 10.50.144.24 | MBUS Orlando | 36.94 | 2020-08 | 2020-08 | 24.06 | APCRBC155 | 82.34 | 91.9
RBD-Doral-UPS1 | Smart-UPS SRT 1500 | AS2108195654 | v1.3.3.1 | 10.28.44.23 | RBG Doral | 38.14 | 2021-02 | 2021-02 | 26.59 | APCRBC155 | 48.78 | 50.7 | Lower the battery temperature to 25 degrees C | 2025-05-15 | 2025-07-12
RCCB-STOCKTON-UPS2 | Smart-UPS 750 | AS1905243282 | v6.5.6 | 10.51.48.65 | RCCB Stockton | 38.26 | 2019-01 | 2019-01 | 26.1 | RBC123 | 38 | 39 | Replace battery, Lower the battery temperature to 25 degrees C
apcB6D7C0 | Smart-UPS 2200 | AS1346243706 | v6.0.6 | 192.168.80.101 | MBCAN Winniepeg | 38.68 | 2013-11 | 2021-11 | 22.19 | RBC43 | 7.62 | 8 | Replace UPS | 2027-05-29 | 2027-05-29
MBUS-Sumner-MDF-UPS1 | Smart-UPS SRT 5000 | AS2315272267 | v2.0.0.6 | 10.50.106.119 | MBUS Sumner | 38.78 | 2023-04 | 2021-07 | 30.01 | APCRBC140 | 22.11 | 28.7 | Lower the battery temperature to 25 degrees C | 2025-02-07 | 2025-06-22
GLCCD-Milwaukee-UPS-SW6 | Smart-UPS 750 | AS1823330636 | v7.1.2 | 10.20.219.223 | GLCCD Milwaukee | 38.93 | 2018-06 | 2018-11 | 24.78 | RBC123 | 12.32 | 14.3 | Replace battery
apc249928 | Smart-UPS 1500 | AS1929241931 | v7.1.2 | 10.52.66.87 | RBG Bakersfield | 39 | 2019-07 | 2019-07 | 24.56 | APCRBC133 | 34.81 | 36.4 | Lower the battery temperature to 25 degrees C
GLCCD-Niles-UPS-MRC-3rdFloor | Smart-UPS 750 | AS1829144758 | v7.1.2 | 10.44.2.186 | GLCCD Niles | 39.24 | 2018-07 | 2020-04 | 26.5 | RBC123 | 72.58 | 78 | Lower the battery temperature to 25 degrees C | 2024-10-31 | 2024-11-20
rh-wpb-airport-ups2 | Smart-UPS SRT 1500 | AS2137294351 | v1.3.3.1 | 10.49.216.24 | RH West Palm Beach | 39.31 | 2021-09 | 2021-09 | 30.25 | APCRBC155 | 23.87 | 25.7 | Lower the battery temperature to 25 degrees C | 2026-03-24 | 2026-03-31
apc24A380 | Smart-UPS 1500 | AS1929241926 | v7.1.2 | 10.52.66.189 | RBG Bakersfield | 39.95 | 2019-07 | 2019-07 | 24.3 | APCRBC133 | 27.22 | 29.2 | Lower the battery temperature to 25 degrees C | 2024-07-03 | 2024-07-09
apc3E3C05 | Smart-UPS 750 | AS2033142980 | v7.1.2 | 10.20.38.57 | RBG Pompano | 40 | 2020-08 | 2020-08 | 27.64 | RBC123 | 54.4 | 57.2 | Lower the battery temperature to 25 degrees C
rbd-richmond-ups2 | Smart-UPS SRT 1500 | AS2122295843 | v1.3.3.1 | 10.46.144.24 | RBG Richmond-VA | 40.09 | 2021-06 | 2021-06 | 27.91 | APCRBC155 | 22.91 | 25.5 | Lower the battery temperature to 25 degrees C | 2025-11-26 | 2026-02-10
MBUS-SaltLakeCity-IDF-UPS-1 | Smart-UPS 1500 RM | R2110192E09003 | v6.6.4 | 172.16.21.230 | MBUS Salt Lake City | 40.12 | 2009-07 | 2021-11 | 25.64 |  | 21.12 | 25.3 | Replace UPS, Lower the battery temperature to 25 degrees C | 2027-03-16 | 2027-07-25
apc22CEC5 | Smart-UPS 1500 | AS1922240763 | v7.1.2 | 10.51.98.87 | RBG Chico | 40.17 | 2019-05 | 2019-05 | 23.56 | APCRBC133 | 28.55 | 30 | Replace battery
apc22CCDE | Smart-UPS 1500 | AS1922240793 | v7.1.2 | 10.51.66.72 | RBG San Francisco | 40.41 | 2019-05 | 2019-05 | 23.43 | APCRBC133 | 65.13 | 67.7 | Replace battery
RBG-Huntington-Beach-UPS2 | Smart-UPS SRT 1500 | AS2040195005 | v6.8.2 | 10.28.92.24 | RBG Huntington Beach | 40.57 | 2020-10 | 2020-10 | 23.81 | APCRBC155 | 16.02 | 16.7 |  | 2024-07-29 | 2024-07-29
apc0D92AA | Smart-UPS X 1500 | AS1825167530 | v6.5.0 | 10.47.35.105 | RCCB Benicia | 40.7 | 2018-06 | 2018-06 | 23.32 | APCRBC115 | 3.51 | 3.6 | Replace battery
mbcan-calgary-ups1 | Smart-UPS SRT 1500 | AS2137292169 | v1.3.3.1 | 10.28.130.23 | MBCAN Calgary | 40.77 | 2021-09 | 2021-09 | 28.42 | APCRBC155 | 13.02 | 13.8 | Lower the battery temperature to 25 degrees C | 2025-11-17 | 2026-03-08
apc0E5BF5 | Smart-UPS 750 | AS1828131640 | v7.1.2 | 10.46.146.156 | RBG Richmond-VA | 40.87 | 2018-07 | 2018-10 | 23.63 | RBC123 | 35.16 | 37 | Replace battery
apc0513B0 | Smart-UPS 1500 | AS1810143088 | v7.1.2 | 10.20.45.97 | RBG Doral | 40.89 | 2018-03 | 2018-03 | 20.21 | APCRBC133 | 44.8 | 46.1 | Replace battery
apc0555FD | Smart-UPS 1500 | AS1811243324 | v7.1.2 | 10.20.44.117 | RBG Doral | 40.94 | 2018-03 | 2018-03 | 20.2 | APCRBC133 | 31.13 | 32.6 | Replace battery
GLCCD-FLINT-UPS-IDFB-1stFlSales | Smart-UPS 2200 | AS2103163318 | v1.3.3.1 | 10.44.163.229 | GLCCD Flint | 41.2 | 2021-01 | 2021-01 | 21.18 | RBC43 | 21.8 | 22.7 |  | 2026-10-09 | 2026-10-14
MBCAN-Brampton-UPS1 | Smart-UPS SRT 1500 | AS2137192336 | v1.3.3.1 | 10.28.128.23 | MBCAN Brampton | 41.35 | 2021-09 | 2021-09 | 21.16 | APCRBC155 | 18.31 | 21 |  | 2027-02-17 | 2027-02-17
GLCCD-VanBuren-UPS-SD2 | Smart-UPS SRT 1500 | AS2032292985 | v7.1.2 | 10.44.208.24 | GLCCD Van Buren | 42.11 | 2020-08 | 2020-08 | 25.04 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2026-01-13 | 2026-02-04
apc233011 | Smart-UPS 750 | AS1924131694 | v7.1.2 | 10.51.66.73 | RBG San Francisco | 42.11 | 2019-06 | 2019-06 | 24.88 | RBC123 | 34.67 | 35.8
apc3DA128 | Smart-UPS SRT 1500 | AS2032293006 | v7.1.2 | 172.16.76.15 | RBG Orlando | 42.12 | 2020-08 | 2020-08 | 23.9 | APCRBC155 | 16.52 | 17.2 |  | 2024-12-13 | 2024-12-13
RCCB-SanLeandroWicks-UPS-SD2 | Smart-UPS SRT 1500 | AS2122393545 | v1.3.3.1 | 10.48.160.5 | RCCB San Leandro | 42.13 | 2021-06 | 2021-06 | 28.52 | APCRBC155 | 21.13 | 29.1 | Lower the battery temperature to 25 degrees C | 2026-08-15 | 2027-01-22
RCCB-SanLeandroWicks-UPS-SD1 | Smart-UPS SRT 1500 | AS2122393543 | v1.3.3.1 | 10.48.160.4 | RCCB San Leandro | 42.14 | 2021-06 | 2021-06 | 28.51 | APCRBC155 | 20.08 | 21.1 | Lower the battery temperature to 25 degrees C | 2026-08-25 | 2027-01-21
MBUS-Conroe-MDF-UPS2 | Smart-UPS SRT 1500 | AS2122295869 | v1.3.3.1 | 10.50.176.125 | MBUS Conroe | 42.23 | 2021-06 | 2021-06 | 27.48 | APCRBC155 | 22.12 | 31 | Lower the battery temperature to 25 degrees C | 2026-06-06 | 2026-09-28
RBD-Gardena-UPS2 | Smart-UPS 750 | AS2109142573 | v1.3.3.1 | 10.57.170.145 | RBG Gardena | 42.23 | 2021-03 | 2021-03 | 22.63 | RBC123 | 56 | 57.2 |  | 2025-01-10 | 2025-01-10
apc6B7F75 | Smart-UPS 750 | 3S2150X13996 | v2.0.0.6 | 10.56.42.244 | RBG Kona | 42.26 | 2021-12 | 2022-03 | 31.45 | APCRBC123 | 28.71 | 29.3 | Lower the battery temperature to 25 degrees C | 2025-01-07 | 2025-06-07
GLCCD-Milwaukee-UPS-SW3-IDF3 | Smart-UPS 750 | AS2137140222 | v1.3.3.1 | 10.20.218.168 | GLCCD Milwaukee | 42.45 | 2021-09 | 2021-12 | 32.39 | RBC123 | 50.34 | 52.6 | Lower the battery temperature to 25 degrees C | 2025-05-15 | 2025-12-30
MBUS-Coatsville-MDF-UPS3 | Smart-UPS X 3000 | AS1822152672 | v6.5.0 | 10.20.54.228 | MBUS Coatesville | 42.7 | 2018-05 | 2018-05 | 20.7 | APCRBC117 | 7.59 | 8.4 | Replace battery
apc1919D3 | Smart-UPS 750 | AS1905243280 | v7.1.2 | 10.51.34.164 | RBG San Jose | 42.94 | 2019-01 | 2019-01 | 23.41 | RBC123 | 41.11 | 46.1 | Replace battery
apc22CEAD | Smart-UPS 1500 | AS1922240750 | v7.1.2 | 10.51.98.88 | RBG Chico | 43 | 2019-05 | 2019-05 | 21.73 | APCRBC133 | 0 | 0 | Replace battery
RCCB-Rancho-UPS2 | Smart-UPS SRT 1500 | AS2040195007 | v6.8.2 | 10.48.112.24 | RCCB Rancho | 43.32 | 2020-10 | 2020-10 | 25.39 | APCRBC155 | 31.99 | 33 | Lower the battery temperature to 25 degrees C
MBUS-Lexington-IDF1-UPS1 | Smart-UPS 1000 | 3S1831X15298 | v6.5.0 | 10.50.50.171 | MBUS Lexington | 43.35 | 2018-08 | 2023-01 | 30.74 | APCRBC132 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2026-10-12 | 2028-02-21
RCCB-Tullahoma-DC-UPS-SD1 | Smart-UPS SRT 1500 | AS2128290918 | v1.3.3.1 | 10.53.16.23 | GLCCD Tullahoma-DC | 43.45 | 2021-07 | 2021-07 | 28.54 | APCRBC155 | 19.92 | 21.3 | Lower the battery temperature to 25 degrees C | 2026-07-04 | 2027-02-19
apc3D56E4 | Smart-UPS SRT 1500 | AS2032292980 | v7.1.2 | 172.16.76.16 | RBG Orlando | 43.51 | 2020-08 | 2020-08 | 23.87 | APCRBC155 | 31.94 | 32.7 |  | 2025-02-22 | 2025-02-22
apc22CEC8 | Smart-UPS 1500 | AS1922240746 | v7.1.2 | 10.46.114.178 | RBG Santa Fe Springs | 43.62 | 2019-05 | 2019-05 | 23.5 | APCRBC133 | 37.98 | 39 | Replace battery | 2025-01-17 | 2025-01-17
apc22CF03 | Smart-UPS 1500 | AS1922240792 | v7.1.2 | 10.51.64.51 | RBG San Francisco | 43.65 | 2019-05 | 2019-05 | 21.19 | APCRBC133 | 18.48 | 61.1 | Replace battery
apc22CD15 | Smart-UPS 1500 | AS1922240860 | v7.1.2 | 10.20.39.46 | RBG Pompano | 43.86 | 2019-05 | 2019-05 | 20.99 | APCRBC133 | 36.58 | 46.1 | Replace battery
MBUS-Lexington-MDF-ADT-UPS1 | SMART-UPS X1500 | AS2121265573 | v6.9.6 | 10.50.50.111 | MBUS Lexington | 43.89 | 2021-05 | 2021-08 | 29.55 | APCRBC115 | 12.55 | 13.3 | Lower the battery temperature to 25 degrees C | 2026-04-22 | 2027-02-10
GLCCD-Rhinelander-UPS | Smart-UPS 1500 | AS2112132091 | v1.3.3.1 | 10.20.224.221 | GLCCD Rhinelander | 44.3 | 2021-03 | 2021-03 | 22.35 | APCRBC133 | 31.11 | 32.5 |  | 2025-10-14 | 2025-10-14
GLCCD-Clarkesville-UPS | Smart-UPS 750 | AS2135132060 | v1.3.3.1 | 10.53.34.229 | GLCCD Clarksville | 44.46 | 2021-09 | 2022-03 | 31.2 | RBC123 | 37.05 | 40.3 | Lower the battery temperature to 25 degrees C | 2025-05-17 | 2026-01-07
GLCCD-Tullahoma-PC-UPS1 | Smart-UPS 2200 | AS2230152866 | v2.0.0.6 | 10.53.2.44 | GLCCD Tullahoma-PC | 44.65 | 2022-07 | 2022-12 | 25.68 | RBC43 | 104.15 | 121 | Lower the battery temperature to 25 degrees C | 2027-11-06 | 2027-12-05
RCCB-Rancho-UPS1 | Smart-UPS SRT 1500 | AS2040195002 | v6.8.2 | 10.48.112.23 | RCCB Rancho | 44.85 | 2020-10 | 2020-10 | 25.06 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C
RCCB-STOCKTON-UPS1 | Smart-UPS 750 | AS1905243281 | v6.5.6 | 10.51.48.75 | RCCB Stockton | 44.99 | 2019-01 | 2019-01 | 20.89 | RBC123 | 35.77 | 37 | Replace battery
rbd-richmond-ups1 | Smart-UPS SRT 1500 | AS2129292955 | v1.3.3.1 | 10.46.144.23 | RBG Richmond-VA | 45.3 | 2021-07 | 2021-07 | 27.64 | APCRBC155 | 23.74 | 25.3 | Lower the battery temperature to 25 degrees C | 2026-11-30 | 2027-03-21
apc1927F8 | Smart-UPS 750 | AS1905243295 | v7.1.2 | 10.51.34.135 | RBG San Jose | 45.57 | 2019-01 | 2019-01 | 19.48 | RBC123 | 32.63 | 33.9 | Replace battery
MBUS-SaltLakeCity-IDF-UPS-2 | Smart-UPS 1500 RM | R2109162E07002 | v5.1.3 | 172.16.21.141 | MBUS Salt Lake City | 45.68 | 2007-08 | 2021-10 | 22.56 |  | 14.96 | 15.6 | Replace UPS | 2027-07-06 | 2027-07-06
apc29600A | Smart-UPS 750 | AS1948231305 | v7.1.2 | 10.52.242.66 | RBG Richmond-CA | 45.72 | 2019-11 | 2019-11 | 23.4 | RBC123 | 41.41 | 43
apc5808D0 | Smart-UPS 2200 | AS1350142462 | v7.1.2 | 10.20.100.238 | RBG Summerville | 45.92 | 2013-12 | 2021-01 | 18.19 | RBC43 | 12.09 | 13 | Replace UPS | 2026-10-03 | 2026-10-03
RBD-Gardena-UPS5 | Smart-UPS 750 | AS2109142572 | v1.3.3.1 | 10.57.170.150 | RBG Gardena | 46.2 | 2021-03 | 2021-03 | 25.08 | RBC123 | 35.37 | 36.4 | Lower the battery temperature to 25 degrees C | 2026-10-26 | 2026-10-30
mbcan-calgary-ups2 | Smart-UPS SRT 1500 | AS2137292172 | v1.3.3.1 | 10.28.130.24 | MBCAN Calgary | 46.32 | 2021-09 | 2021-09 | 26.59 | APCRBC155 | 19.01 | 20 | Lower the battery temperature to 25 degrees C | 2026-04-05 | 2026-05-24
MBUS-Sumner-IDF1-UPS | Smart-UPS 1500 | AS2307134662 | v2.0.0.6 | 10.50.106.118 | MBUS Sumner | 46.38 | 2023-02 | 2023-05 | 38.99 | APCRBC133 | 32.24 | 33 | Lower the battery temperature to 25 degrees C | 2025-05-13 | 2027-01-10
RCCB-STOCKTON-UPS3 | Smart-UPS 1500 | AS1922330008 | v6.6.4 | 10.51.48.99 | RCCB Stockton | 46.4 | 2019-05 | 2019-05 | 19.32 | APCRBC133 | 0 | 0 | Replace battery | 2024-08-12 | 2024-08-12
RCCB-VENTURA-UPS-MDF | Smart-UPS 3000 | AS2115265766 | v1.3.3.1 | 10.49.96.118 | RCCB Ventura | 46.72 | 2021-04 | 2021-04 | 24.24 | RBC43 | 7 | 7.1 |  | 2026-11-06 | 2026-11-06
apc267179 | Smart-UPS 750 | AS1936145174 | v7.1.2 | 10.52.66.152 | RBG Bakersfield | 46.79 | 2019-09 | 2019-09 | 21.69 | RBC123 | 76.46 | 79.3
apc331213 | Smart-UPS SRT 1500 | AS2016190974 | v7.1.2 | 10.52.34.235 | RBG Evansville | 46.83 | 2020-04 | 2020-04 | 22.23 | APCRBC155 | 13.96 | 14.2 |  | 2025-02-18 | 2025-02-18
RCCB-Sacramental-UPS-MDF-NVR | Smart-UPS 3000 | AS2115265963 | v1.3.3.1 | 10.47.178.216 |  | 47.07 | 2021-04 | 2021-04 | 19.85 | RBC43 | 11.23 | 11.7
apc71B0E8 | Smart-UPS SRT 1500 | AS2226193012 | v2.0.0.6 | 10.46.26.156 | MBCAN Mississauga | 47.11 | 2022-06 | 2022-06 | 26.78 | APCRBC155 | 33.97 | 38.9 | Lower the battery temperature to 25 degrees C | 2025-05-14 | 2025-08-23
RCCB-LOS-ANGELES-UPS-SD2 | Smart-UPS SRT 1500 | AS2122393556 | v1.3.3.1 | 10.47.208.8 | RCCB Los Angeles | 47.26 | 2021-06 | 2021-06 | 25 | APCRBC155 | 66.47 | 69.3 |  | 2025-12-13 | 2025-12-13
apc233865 | Smart-UPS 750 | AS1924131705 | v7.1.2 | 10.51.66.70 | RBG San Francisco | 47.31 | 2019-06 | 2019-06 | 17.64 | RBC123 | 59.13 | 61.8
apc2302A1 | Smart-UPS 750 | AS1924131711 | v7.1.2 | 10.51.66.80 | RBG San Francisco | 47.31 | 2019-06 | 2019-06 | 17.66 | RBC123 | 75 | 76.8
apc232FF8 | Smart-UPS 750 | AS1924131701 | v7.1.2 | 10.51.128.96 | RBG West Sacramento | 47.45 | 2019-06 | 2019-06 | 24.03 | RBC123 | 57.99 | 61.8 |  | 2025-03-03 | 2025-03-03
GLCCD-Tullahoma-PC-UPS2 | Smart-UPS 750 | AS2137140217 | v1.3.3.1 | 10.53.2.45 | GLCCD Tullahoma-PC | 47.54 | 2021-09 | 2022-11 | 28.43 | RBC123 | 70.35 | 73.4 | Lower the battery temperature to 25 degrees C | 2026-10-05 | 2027-05-27
GLCCD-Milwaukee-UPS-SW8-SD2-114 | Smart-UPS SRT 1500 | AS2032292977 | v7.1.2 | 10.20.218.14 | GLCCD Milwaukee | 48 | 2020-08 | 2020-08 | 21.71 | APCRBC155 | 29.04 | 29.9 |  | 2024-09-15 | 2024-09-15
RBD-Gardena-UPS3 | Smart-UPS 750 | AS2109142554 | v1.3.3.1 | 10.57.170.148 | RBG Gardena | 48.03 | 2021-03 | 2021-03 | 23.05 | RBC123 | 24.79 | 26 |  | 2026-09-18 | 2026-09-28
RBD-Centreville-UPS1 | Smart-UPS 750 | AS2113162309 | v1.3.3.1 | 10.54.90.58 | RBG Centreville | 48.11 | 2021-04 | 2021-04 | 28.54 | RBC123 | 56.94 | 59.1 | Lower the battery temperature to 25 degrees C | 2025-04-05 | 2025-06-29
apc65332C | Smart-UPS 750 | 3S2205X12359 | v2.0.0.6 | 10.54.250.108 | RBG Austin | 48.15 | 2022-02 | 2022-05 | 31.09 | APCRBC123 | 71.73 | 75 | Lower the battery temperature to 25 degrees C | 2025-02-26 | 2025-06-25
apc22CCC1 | Smart-UPS 1500 | AS1922240791 | v7.1.2 | 10.51.34.191 | RBG San Jose | 48.23 | 2019-05 | 2019-05 | 16.84 | APCRBC133 | 58.07 | 60.4 | Replace battery | 2024-09-15 | 2024-09-15
rccb-flintmidc-ups2 | Smart-UPS SRT 1500 | AS2246190052 | v2.0.0.6 | 10.44.160.24 | GLCCD Flint | 48.28 | 2022-11 | 2022-11 | 30.55 | APCRBC155 | 58.74 | 61 | Lower the battery temperature to 25 degrees C | 2026-03-14 | 2027-05-03
GLCCD-MadisonWindsor-UPS-MDF | Smart-UPS 3000 | AS2110155189 | v1.3.3.1 | 10.20.228.113 | GLCCD Madison | 48.93 | 2021-03 | 2021-03 | 23.3 | RBC43 | 0 | 0 |  | 2026-07-15 | 2026-12-02
RBD-Redding-IDF1-UPS2 | Smart-UPS 750 | AS2053340851 | v6.8.2 | 10.54.42.12 | RBG Redding | 49.09 | 2020-12 | 2020-12 | 29.06 | RBC123 | 60.56 | 63 | Lower the battery temperature to 25 degrees C | 2026-01-05 | 2026-03-02
apc22BC9C | Smart-UPS 1500 | AS1922240828 | v7.1.2 | 10.51.128.92 | RBG West Sacramento | 49.36 | 2019-05 | 2019-05 | 18.95 | APCRBC133 | 93.56 | 100.1 | Replace battery | 2025-02-04 | 2025-02-04
MBUS-OklahomaCity-MDF-UPS1 | Smart-UPS 750 | AS2303332738 | v2.0.0.6 | 10.50.173.254 | MBUS Oklahoma City | 49.42 | 2023-01 | 2023-04 | 30.07 | APCRBC123 | 18.3 | 196.7 | Lower the battery temperature to 25 degrees C | 2026-06-03 | 2027-11-06
apc3E66C5 | Smart-UPS 750 | AS2033142948 | v7.1.2 | 10.20.39.70 | RBG Pompano | 49.55 | 2020-08 | 2020-08 | 22.62 | RBC123 | 48.01 | 52
apc295E8D | Smart-UPS 750 | AS1948231278 | v7.1.2 | 10.52.242.161 | RBG Richmond-CA | 49.83 | 2019-11 | 2019-11 | 22.77 | RBC123 | 45.81 | 47.4 |  | 2025-01-17 | 2025-01-17
apcB6D7AF | Smart-UPS 2200 | AS1348244031 | v6.0.6 | 10.20.128.50 | MBCAN Brampton | 49.89 | 2013-11 | 2022-07 | 19.85 | RBC43 | 6.42 | 7 | Replace UPS | 2028-02-21 | 2028-02-21
RCCB-IRVINE-UPS | Smart-UPS X 3000 | AS2105250143 | v1.3.3.1 | 10.47.66.154 |  | 49.9 | 2021-02 | 2021-02 | 25.73 | APCRBC117 | 33.9 | 34.9 | Lower the battery temperature to 25 degrees C
apc233849 | Smart-UPS 750 | AS1924131709 | v7.1.2 | 10.46.114.64 | RBG Santa Fe Springs | 50.14 | 2019-06 | 2019-06 | 20.7 | RBC123 | 22.12 | 24 |  | 2025-02-10 | 2025-02-10
RBD-Pompano-UPS2 | Smart-UPS SRT 1500 | AS2111290863 | v1.3.3.1 | 10.28.38.24 | RBG Pompano | 50.18 | 2021-03 | 2021-03 | 24.5 | APCRBC155 | 8.44 | 20.7 |  | 2026-06-01 | 2026-06-01
GLCCD-EauClaire-UPS | Smart-UPS 3000 | AS2041362179 | v7.1.2 | 10.20.212.188 | GLCCD Eau Claire | 50.32 | 2020-10 | 2020-10 | 21.24 | RBC43 | 9.8 | 9.8 |  | 2026-04-09 | 2026-04-09
MBUS-StJohns-IDF1-UPS1 | Smart-UPS 1000 | 3S2224X16443 | v2.0.0.6 | 10.20.52.121 | MBUS St Johns | 50.34 | 2022-06 | 2022-09 | 31.95 | APCRBC132 | 63.17 | 64.1 | Lower the battery temperature to 25 degrees C | 2025-11-12 | 2026-12-06
rccb-sylmar-UPS1 | Smart-UPS SRT 1500 | AS2122295837 | v1.3.3.1 | 10.49.0.23 | RCCB Sylmar | 50.37 | 2021-06 | 2021-06 | 25.1 | APCRBC155 | 25.19 | 26 | Lower the battery temperature to 25 degrees C | 2026-10-17 | 2026-10-25
MBUS-CID-IDF8-UPS | Smart-UPS 750 | AS2136130059 | v1.3.3.1 | 10.50.138.242 | MBUS City of Industry | 50.62 | 2021-09 | 2021-09 | 5.35 | RBC123 | 50.95 | 52 |  | 2025-09-29 | 2025-09-29
RCCB-Las-Vegas-UPS1 | Smart-UPS SRT 1500 | AS2051292102 | v1.3.3.1 | 10.47.224.7 | RCCB Las Vegas | 51.01 | 2020-12 | 2020-12 | 22.17 | APCRBC155 | 36.49 | 40.4 |  | 2025-01-07 | 2025-01-07
GLCCD-Kincheloe-UPS | Smart-UPS SRT 1500 | AS2132190732 | v1.3.3.1 | 10.45.114.228 | GLCCD Kincheloe | 51.08 | 2021-08 | 2021-08 | 21.71 | APCRBC155 | 6.96 | 7.2
apc3E2611 | Smart-UPS 750 | AS2033142978 | v7.1.2 | 10.20.39.50 | RBG Pompano | 51.49 | 2020-08 | 2020-08 | 21.94 | RBC123 | 64.94 | 73.4 |  | 2024-08-22 | 2024-08-22
RBD-Redding-MDF-UPS1 | Smart-UPS SRT 1500 | AS2016190972 | v6.8.2 | 10.54.42.50 | RBG Redding | 51.59 | 2020-04 | 2020-04 | 21 | APCRBC155 | 31.48 | 34.9 |  | 2025-01-10 | 2025-01-10
apc513B2C | Smart-UPS SRT 1500 | AS2122393555 | v1.3.3.1 | 10.48.19.159 | RCCB Salinas | 51.72 | 2021-06 | 2021-06 | 19.75 | APCRBC155 | 0 | 0
RCCB-IRVING-UPS | Smart-UPS X 3000 | AS2203251650 | v1.3.3.1 | 10.47.66.89 | RCCB Irvine | 51.88 | 2022-01 | 2022-01 | 27.55 | APCRBC117 | 0 | 0 | Lower the battery temperature to 25 degrees C
rccb-sylmar-UPS2 | Smart-UPS SRT 1500 | AS2122295838 | v1.3.3.1 | 10.49.0.24 | RCCB Sylmar | 51.9 | 2021-06 | 2021-06 | 24 | APCRBC155 | 18.32 | 19 |  | 2025-12-19 | 2025-12-19
RH Office 7S Switches | Smart-UPS 2200 | AS1952161545 | v6.5.6 | 172.16.231.221 | RH Rosemont 7th Floor | 52.27 | 2019-12 | 2022-11 | 22.82 | RBC43 | 23.54 | 25.3 |  | 2027-01-12 | 2027-01-14
GLCCD-AlsipPC-UPS-SW5-ASRS | Smart-UPS 750 | AS2102143523 | v1.3.3.1 | 10.45.243.141 | GLCCD Alsip | 52.55 | 2021-01 | 2021-01 | 27.01 | RBC123 | 27.88 | 27.9 | Lower the battery temperature to 25 degrees C | 2025-10-03 | 2026-01-30
MBUS-CID-MDF-UPS1 | Smart-UPS SRT 1500 | AS2122194754 | v1.3.3.1 | 10.50.128.7 | MBUS City of Industry | 52.86 | 2021-06 | 2021-06 | 20.33 | APCRBC155 | 7.73 | 8.4
MBUS-Atlanta-MDF-UPS1 | Smart-UPS SRT 1500 | AS2032292986 | v6.8.2 | 10.52.144.18 | MBUS Atlanta | 53.48 | 2020-08 | 2020-08 | 20.99 | APCRBC155 | 21.84 | 23 |  | 2025-03-13 | 2025-03-13
GLCCD-WAUSAU-UPS-MDF | Smart-UPS 3000 | AS2112162683 | v1.3.3.1 | 10.20.226.105 | GLCCD Wausau | 53.55 | 2021-03 | 2021-03 | 21.53 | RBC43 | 10.38 | 10.4 |  | 2026-08-04 | 2026-08-04
apc4E4E21 | Smart-UPS SRT 1500 | AS2009190668 | v7.1.2 | 10.52.242.165 | RBG Richmond-CA | 53.77 | 2020-02 | 2024-04 | 28 | APCRBC155 | 44.64 | 46.6 | Lower the battery temperature to 25 degrees C | 2028-09-02 | 2029-12-08
RBD-Redding-IDF2-UPS3 | Smart-UPS 750 | AS2051242677 | v1.3.3.1 | 10.54.42.13 | RBG Redding | 53.79 | 2020-12 | 2020-12 | 27.21 | RBC123 | 55.99 | 57.8 | Lower the battery temperature to 25 degrees C | 2026-01-02 | 2026-01-22
GLCCD-AlsipPR-UPS-SW4-Shipping | Smart-UPS 750 | AS2110233476 | v1.3.3.1 | 10.45.243.143 | GLCCD Alsip | 53.81 | 2021-03 | 2021-03 | 26.05 | RBC123 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2025-07-13 | 2025-09-14
RCCB-SYLMAR-UPS-MDF | Smart-UPS 3000 | AS2120261951 | v5.1.7 | 10.49.2.221 | RCCB Sylmar | 53.84 | 2021-05 | 2021-05 | 22.04 |  | 14.02 | 14.9 |  | 2026-12-15 | 2026-12-15
RCCB-Tullahoma-DC-UPS-SD2 | Smart-UPS SRT 1500 | AS2128290910 | v1.3.3.1 | 10.53.16.24 | GLCCD Tullahoma-DC | 53.91 | 2021-07 | 2023-02 | 27.6 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2028-01-03 | 2028-09-15
apc5DF558 | Smart-UPS SRT 1500 | AS2147191321 | v1.3.3.1 | 10.57.202.157 | RBG San Diego | 54 | 2021-11 | 2021-11 | 25 | APCRBC155 | 39.02 | 40.3 |  | 2026-08-01 | 2026-08-01
RBD-ChicagoHQ-MDFUPS2 | Smart-UPS SRT 1500 | AS2132290999 | v1.3.3.1 | 10.57.155.58 | RBG Chicago-HQ | 54.05 | 2021-08 | 2021-08 | 24 | APCRBC155 | 49.41 | 50.5 |  | 2026-01-29 | 2026-01-29
GLCCD-AlsipDC-UPS-MDF-CORE | Smart-UPS 3000 | AS2110155190 | v1.3.3.1 | 10.20.144.228 | GLCCD Alsip | 54.24 | 2021-03 | 2021-03 | 21.33 | RBC43 | 12.44 | 13.6 |  | 2026-07-11 | 2026-07-11
GLCCD-Eagan-UPS-SD1 | Smart-UPS SRT 1500 | AS2115192983 | v1.3.3.1 | 10.28.206.7 | GLCCD Eagan | 54.25 | 2021-04 | 2021-04 | 23.07 | APCRBC155 | 16.68 | 17.5 |  | 2025-11-29 | 2025-11-29
GLCCD-EAGAN-UPS-SD2 | Smart-UPS SRT 1500 | AS2115192981 | v1.3.3.1 | 10.28.206.8 | GLCCD Eagan | 54.37 | 2021-04 | 2021-04 | 24 | APCRBC155 | 17.09 | 17.8 |  | 2026-12-02 | 2026-12-02
apc3E3C54 | Smart-UPS 750 | AS2033142995 | v7.1.2 | 10.20.39.52 | RBG Pompano | 54.47 | 2020-08 | 2020-08 | 23.33 | RBC123 | 51.28 | 53.3 |  | 2025-03-16 | 2025-03-16
MBUS-Lexington-IDF3-UPS1 | Smart-UPS 1000 | 3S2114X12690 | v6.1.1 | 10.50.50.164 | MBUS Lexington | 54.5 | 2021-04 | 2021-07 | 27.06 | APCRBC132 | 33.53 | 34.8 | Lower the battery temperature to 25 degrees C | 2026-01-25 | 2026-04-24
MBUS-Fairfield-MDF-UPS2 | Smart-UPS SRT 1500 | AS2129292952 | v1.3.3.1 | 10.28.56.24 | MBUS Fairfield | 54.54 | 2021-07 | 2021-07 | 24.68 | APCRBC155 | 37.61 | 39.6 |  | 2026-06-17 | 2027-03-01
MBUS-Fairfield-MDF-UPS1 | Smart-UPS SRT 1500 | AS2129192711 | v1.3.3.1 | 10.28.56.23 | MBUS Fairfield | 54.54 | 2021-07 | 2021-07 | 24.69 | APCRBC155 | 41.34 | 55.1 |  | 2026-05-29 | 2027-02-25
apc366F0E | Smart-UPS 750 | AS2025136680 | v7.1.2 | 10.53.178.66 | RBG Monterey | 54.66 | 2020-06 | 2020-06 | 22.29 | RBC123 | 27.3 | 28.7 |  | 2025-01-16 | 2025-01-16
MBUS-Atlanta-MDF-UPS2 | Smart-UPS SRT 1500 | AS2049393677 | v1.3.3.1 | 10.52.144.23 | MBUS Atlanta | 55.63 | 2020-12 | 2020-12 | 21.93 | APCRBC155 | 20.93 | 30.1 |  | 2025-10-10 | 2025-10-10
GLCCD-Milwaukee-UPS-SW8-SD1-120 | Smart-UPS SRT 1500 | AS2034193757 | v7.1.2 | 10.20.218.13 | GLCCD Milwaukee | 55.64 | 2020-08 | 2020-08 | 21 | APCRBC155 | 20.52 | 21.2 |  | 2025-10-29 | 2025-10-29
GLCCD-AlsipDC-UPS-MDF-NVR-TOP | Smart-UPS 1000 | 3S2111X17138 | v7.1.2 | 10.20.144.168 | GLCCD Alsip | 55.77 | 2021-03 | 2021-03 | 25.46 | APCRBC132 | 40.94 | 42.4 | Lower the battery temperature to 25 degrees C | 2025-10-02 | 2025-11-08
GLCCD-Milwaukee-UPS-SW5-135 | Smart-UPS 750 | AS2113230887 | v1.3.3.1 | 10.20.218.169 | GLCCD Milwaukee | 55.9 | 2021-04 | 2021-04 | 28.17 | RBC123 | 40.85 | 41.6 | Lower the battery temperature to 25 degrees C | 2026-09-12 | 2027-01-06
apc65114A | Smart-UPS 750 | 3S2205X12358 | v1.5.1.1 | 10.54.250.168 | RBG Austin | 56.02 | 2022-02 | 2022-05 | 28.78 | APCRBC123 | 12.12 | 13.2 | Lower the battery temperature to 25 degrees C | 2025-07-07 | 2025-12-16
GLCCD-EAGAN-UPS-SW1B-IDF1 | Smart-UPS 750 | AS2304230117 | v2.0.0.6 | 10.27.206.146 | GLCCD Eagan | 56.05 | 2023-01 | 2024-01 | 38.2 | APCRBC123 | 38.37 | 39.4 | Lower the battery temperature to 25 degrees C | 2025-07-30 | 2027-01-05
RCCB-VENTURA-UPS-SD1 | Smart-UPS SRT 1500 | AS2234293830 | v2.0.0.6 | 10.49.96.23 | RCCB Ventura | 56.13 | 2022-08 | 2022-08 | 26.72 | APCRBC155 | 40.97 | 42.6 | Lower the battery temperature to 25 degrees C | 2026-12-16 | 2027-03-14
GLCCD-Niles-UPS-MDF-Rack1-Top | Smart-UPS 3000 | AS2115266389 | v1.3.3.1 | 10.44.3.240 | GLCCD Niles | 56.41 | 2021-04 | 2021-04 | 20.58 | RBC43 | 17.27 | 18.2 |  | 2026-08-23 | 2026-08-23
MBUS-Orlando-IDF5-UPS1 | Smart-UPS 750 | AS2303332737 | v2.0.0.6 | 172.16.27.151 | MBUS Orlando | 56.46 | 2023-01 | 2023-04 | 34.32 | APCRBC123 | 24.52 | 25.3 | Lower the battery temperature to 25 degrees C | 2025-12-18 | 2027-12-03
RCCB-BAKERSFIELD-UPS-SD2 | Smart-UPS SRT 1500 | AS2122194748 | v1.3.3.1 | 10.47.16.24 | RCCB Bakersfield | 56.59 | 2021-06 | 2021-06 | 22.77 | APCRBC155 | 57.57 | 59.1 |  | 2025-11-18 | 2025-11-18
MBUS-Conroe-IDF1-UPS1 | Smart-UPS 1500 | AS2307134476 | v2.0.0.6 | 10.27.22.144 | MBUS Conroe | 56.71 | 2023-02 | 2023-11 | 37.19 | APCRBC133 | 8.57 | 9 | Lower the battery temperature to 25 degrees C | 2026-01-25 | 2028-08-07
MBUS-Conroe-IDF1-UPS3 | Smart-UPS 1500 | AS2307134471 | v2.0.0.6 | 10.27.22.56 | MBUS Conroe | 56.83 | 2023-02 | 2023-11 | 36.06 | APCRBC133 | 15.99 | 16.2 | Lower the battery temperature to 25 degrees C | 2026-02-21 | 2028-07-02
RCCB-Sacremento-UPS-SD2 | Smart-UPS SRT 1500 | AS2122194857 | v1.3.3.1 | 10.47.176.8 | RCCB Sacramento | 56.88 | 2021-06 | 2021-06 | 22.42 | APCRBC155 | 19.12 | 20 |  | 2025-10-03 | 2025-10-03
apc5DF529 | Smart-UPS SRT 1500 | AS2147191323 | v1.3.3.1 | 10.57.202.247 | RBG San Diego | 56.94 | 2021-11 | 2021-11 | 25 | APCRBC155 | 31.98 | 33.4 |  | 2027-08-02 | 2027-08-02
MBUS-DicksonROP-MDF-UPS2 | Smart-UPS SRT 1500 | AS2128290873 | v1.3.3.1 | 10.28.104.24 | MBUS DicksonROP | 57.29 | 2021-07 | 2021-07 | 23.25 | APCRBC155 | 28.05 | 29 |  | 2026-03-09 | 2026-03-09
GLCCD-FLINT-UPS-SD1 | Smart-UPS SRT 1500 | AS2319293061 | v2.0.0.6 | 10.44.160.23 | GLCCD Flint | 57.79 | 2023-05 | 2023-05 | 28.66 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2026-10-06 | 2027-08-14
MBUS-Walker-IDF3-UPS1 | Smart-UPS 1000 | 3S2312X10859 | v2.0.0.6 | 10.44.98.110 | MBUS Walker | 57.88 | 2023-03 | 2024-01 | 41.97 | APCRBC132 | 20.09 | 23.3 | Lower the battery temperature to 25 degrees C | 2025-11-17 | 2028-11-30
MBUS-DicksonROP-MDF-UPS1 | Smart-UPS SRT 1500 | AS2128290872 | v1.3.3.1 | 10.28.104.23 | MBUS DicksonROP | 58.31 | 2021-07 | 2021-07 | 23.86 | APCRBC155 | 34.35 | 43.3 |  | 2027-02-23 | 2027-02-23
MBUS-Phoenix-IDF1-UPS | Smart-UPS 1500 | AS2307332106 | v2.0.0.6 | 10.50.90.242 | MBUS Phoenix | 58.33 | 2023-02 | 2023-10 | 35.39 | APCRBC133 | 68.76 | 72.6 | Lower the battery temperature to 25 degrees C | 2026-05-05 | 2028-07-29
MBUS-Enfield-MDF-UPS1 | Smart-UPS SRT 1500 | AS2122194745 | v1.3.3.1 | 10.45.0.23 | MBUS Enfield | 58.4 | 2021-06 | 2021-06 | 22.53 | APCRBC155 | 29.09 | 30.6 |  | 2025-12-28 | 2025-12-28
apc5131CA | Smart-UPS SRT 1500 | AS2122393568 | v1.3.3.1 | 10.54.250.62 | RBG Austin | 58.46 | 2021-06 | 2021-06 | 23.07 | APCRBC155 | 38.1 | 47.4 |  | 2026-04-10 | 2026-04-10
apc436147 | Smart-UPS 750 | AS2047141612 | v1.1.0.16 | 10.54.2.128 | RBG Moreno Valley | 58.55 | 2020-11 | 2020-11 | 22.42 | RBC123 | 20.81 | 21.4 |  | 2025-07-28 | 2025-07-28
RCCB-DOWNEY-UPS-SD2 | Smart-UPS SRT 1500 | AS2122393538 | v1.3.3.1 | 10.47.112.34 | RCCB Downey | 58.73 | 2021-06 | 2021-06 | 21.85 | APCRBC155 | 54.49 | 57.2 |  | 2025-03-17 | 2025-03-17
RBD-Gardena-UPS1 | Smart-UPS SRT 1500 | AS2103193798 | v1.3.3.1 | 10.57.170.146 | RBG Gardena | 58.85 | 2021-01 | 2021-01 | 22 | APCRBC155 | 55.36 | 57.1 |  | 2026-06-06 | 2026-06-06
MBUS-Pompano3PL-MDF-UPS1 | Smart-UPS SRT 1500 | AS2322192684 | v2.0.0.6 | 10.61.98.219 | MBUS Pompano | 58.92 | 2023-06 | 2023-06 | 26.11 | APCRBC155 | 9.01 | 9.7 | Lower the battery temperature to 25 degrees C | 2024-11-25 | 2024-11-29
RCCB-Sacramento-UPS-SD1 | Smart-UPS SRT 1500 | AS2122194749 | v1.3.3.1 | 10.47.176.7 | RCCB Sacramento | 59.04 | 2021-06 | 2021-06 | 23.05 | APCRBC155 | 31.79 | 32.9 |  | 2026-12-16 | 2026-12-16
apc75A8B4 | Smart-UPS X 3000 | AS2240154599 | v2.0.0.6 | 172.16.232.123 | RH Rosemont 8th Floor | 59.05 | 2022-10 | 2022-10 | 28.22 | APCRBC143 | 13.7 | 14.4 | Lower the battery temperature to 25 degrees C | 2027-06-13 | 2028-01-29
RCCB-Sylmar-UPS-SW2-IDF-WH | Smart-UPS 1000 | 3S2204X19300 | v2.0.0.6 | 10.49.3.16 | RCCB Sylmar | 59.56 | 2022-01 | 2022-04 | 26.36 | APCRBC132 | 35.89 | 36.4 | Lower the battery temperature to 25 degrees C
GLCCD-AlsipPR-UPS-MDS-NVR | Smart-UPS 3000 | AS2115167193 | v1.3.3.1 | 10.45.243.229 | GLCCD Alsip | 59.58 | 2021-04 | 2021-04 | 20.16 | RBC43 | 20.21 | 22.7 |  | 2026-07-30 | 2026-07-30
GLCCD-Caledonia-IDF3-UPS6 | Smart-UPS 750 | AS2047141601 | v1.1.0.16 | 10.58.10.16 | GLCCD Caledonia | 59.58 | 2020-11 | 2020-11 | 24.33 | RBC123 | 86.45 | 89 |  | 2026-02-07 | 2026-02-11
GLCCD-GrandRapids-UPS-MDF2 | Smart-UPS 2200 | AS2230152865 | v2.0.0.6 | 10.45.202.253 | GLCCD Grand Rapids | 59.67 | 2022-07 | 2023-12 | 31.84 | RBC43 | 32.84 | 35.1 | Lower the battery temperature to 25 degrees C | 2029-02-04 | 2029-02-22
MBUS-McCook-MDF-UPS1 | Smart-UPS SRT 1500 | AS2235191964 | v2.0.0.6 | 10.50.0.23 | MBUS McCook | 59.77 | 2022-08 | 2022-08 | 19.82 | APCRBC155 | 31.69 | 33.6 |  | 2027-05-05 | 2027-05-05
GLCCD-Milwaukee-UPS-SW4-IDF4 | Smart-UPS 1500 | AS2303165863 | v2.0.0.6 | 10.20.218.175 | GLCCD Milwaukee | 59.81 | 2023-01 | 2023-04 | 31.05 | APCRBC133 | 25.53 | 26.3 | Lower the battery temperature to 25 degrees C | 2026-07-08 | 2027-11-27
MBUS-Garner-XXX-UPS1 | Smart-UPS 1000 | 3S1832X18832 | v6.5.0 | 10.50.42.101 | MBUS Garner | 59.81 | 2018-08 | 2023-11 | 27.46 | APCRBC132 | 49.24 | 55.4 | Lower the battery temperature to 25 degrees C | 2028-02-06 | 2029-01-09
MBUS-McCook-MDF-UPS2 | Smart-UPS SRT 1500 | AS2235292683 | v2.0.0.6 | 10.50.0.24 | MBUS McCook | 60.02 | 2022-08 | 2022-08 | 19.34 | APCRBC155 | 0 | 0 |  | 2027-05-08 | 2027-05-08
MBUS-McCook-IDF4-UPS | SMART-UPS X1000 | AS2228160166 | v2.0.0.6 | 10.50.10.219 | MBUS McCook | 60.06 | 2022-07 | 2022-10 | 28.16 | APCRBC116 | 24.64 | 30.4 | Lower the battery temperature to 25 degrees C | 2027-07-08 | 2028-03-26
GLCCD-AlsipDC-UPS-MDF-SW1 | Smart-UPS 3000 | AS2110155187 | v1.3.3.1 | 10.20.145.45 | GLCCD Alsip | 60.12 | 2021-03 | 2021-09 | 20.21 | RBC43 | 19.06 | 20.1 |  | 2026-08-16 | 2026-08-16
GLCCD-GrandRapids-UPS-MDF1 | Smart-UPS 2200 | AS2315261711 | v2.0.0.6 | 10.45.192.106 | GLCCD Grand Rapids | 60.45 | 2023-04 | 2023-12 | 40.27 | RBC43 | 7.6 | 69.6 | Lower the battery temperature to 25 degrees C | 2028-08-07 | 2028-10-09
MBUS-Stockton-IDF2-UPS1 | Smart-UPS 1500 | AS2307331923 | v2.0.0.6 | 172.16.24.241 | MBUS Stockton | 60.57 | 2023-02 | 2023-05 | 33.26 | APCRBC133 | 46.68 | 47.4 | Lower the battery temperature to 25 degrees C | 2027-05-17 | 2028-09-10
GLCCD-Elizabethtown-UPS | Smart-UPS 750 | AS2123141732 | v1.3.3.1 | 10.53.50.252 | GLCCD Elizabethtown | 60.77 | 2021-06 | 2022-02 | 28.3 | RBC123 | 23.21 | 31.8 | Lower the battery temperature to 25 degrees C | 2027-02-13 | 2027-10-27
MBUS-Walker-MDF-UPS1 | Smart-UPS SRT 1500 | AS2108195658 | v1.3.3.1 | 10.44.96.13 | MBUS Walker | 60.77 | 2021-02 | 2021-02 | 18.97 | APCRBC155 | 32.76 | 41.8 |  | 2025-05-20 | 2025-05-20
GLCCD-Niles-UPS-MDF-Rack6 | Smart-UPS 3000 | AS2115266383 | v1.3.3.1 | 10.44.2.147 | GLCCD Niles | 60.91 | 2021-04 | 2021-12 | 20.82 | RBC43 | 13.63 | 14.9 |  | 2027-07-03 | 2027-07-03
RBD-Chantilly-UPS2 | Smart-UPS SRT 1500 | AS2111290924 | v1.3.3.1 | 10.28.76.8 | RBG Chantilly | 61.14 | 2021-03 | 2021-03 | 20.6 | APCRBC155 | 17.37 | 18 |  | 2025-11-18 | 2025-11-18
MBUS-Phoenix-IDF3-UPS | Smart-UPS 750 | AS2303332731 | v2.0.0.6 | 10.50.90.253 | MBUS Phoenix | 61.16 | 2023-01 | 2023-04 | 33.7 | APCRBC123 | 18.31 | 19.1 | Lower the battery temperature to 25 degrees C | 2026-12-15 | 2028-07-28
apc52AB1D | Smart-UPS 750 | AS2128141003 | v1.3.3.1 | 10.49.145.217 | RH Waukegan | 61.34 | 2021-07 | 2021-07 | 25.48 | RBC123 | 7.1 | 7.1 | Lower the battery temperature to 25 degrees C | 2026-05-18 | 2026-07-23
apc71B130 | Smart-UPS SRT 1500 | AS2226193002 | v2.0.0.6 | 10.46.26.251 | MBCAN Mississauga | 61.47 | 2022-06 | 2022-06 | 25.12 | APCRBC155 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2027-03-26 | 2027-11-05
MBUS-Harriman-MDF-UPS1 | Smart-UPS SRT 1500 | AS2128290911 | v1.3.3.1 | 10.50.224.23 | MBUS Harriman | 62.17 | 2021-07 | 2021-07 | 22.95 | APCRBC155 | 69.95 | 83.8 |  | 2027-01-27 | 2027-01-27
MBUS-Conroe-MDF-UPS3 | Smart-UPS 2200 | AS2325331342 | v2.0.0.6 | 10.27.22.57 | MBUS Conroe | 62.23 | 2023-06 | 2023-06 | 27.49 | RBC43 | 29.22 | 30 | Lower the battery temperature to 25 degrees C | 2026-07-02 | 2026-09-26
RBD-Chantilly-UPS1 | Smart-UPS SRT 1500 | AS2111190719 | v1.3.3.1 | 10.28.76.7 | RBG Chantilly | 62.33 | 2021-03 | 2021-03 | 21.7 | APCRBC155 | 61.12 | 66.6 |  | 2026-11-03 | 2026-11-05
apc513254 | Smart-UPS SRT 1500 | AS2122293193 | v1.3.3.1 | 10.54.250.57 | RBG Austin | 62.41 | 2021-06 | 2021-06 | 22.05 | APCRBC155 | 26.14 | 27.6 |  | 2026-06-07 | 2026-06-07
RCCB-BAKERSFIELD-MDF | Smart-UPS 3000 | AS2052162833 | v6.4.0 | 10.47.18.221 | RCCB Bakersfield | 62.57 | 2020-12 | 2020-12 | 18.25 | RBC43 | 9.55 | 10.4
apc7488E4 | Smart-UPS SRT 1500 | AS2234293709 | v2.0.0.6 | 10.56.26.58 | RBG Hilo | 62.7 | 2022-08 | 2022-08 | 25 | APCRBC155 | 21.33 | 29.4 |  | 2027-04-26 | 2027-04-26
MBUS-Conroe-IDF8-UPS1 | Smart-UPS 1500 | AS2307331969 | v2.0.0.6 | 10.27.22.59 | MBUS Conroe | 62.83 | 2023-02 | 2023-11 | 32.52 | APCRBC133 | 13.2 | 13.7 | Lower the battery temperature to 25 degrees C | 2026-10-27 | 2028-10-13
GLCCD-FLINT-UPS-Loft-WH-VP | Smart-UPS 750 | AS2109142570 | v1.3.3.1 | 10.44.163.230 | GLCCD Flint | 62.86 | 2021-03 | 2021-03 | 24.55 | RBC123 | 27.4 | 27.9 |  | 2026-10-31 | 2026-11-23
RBD-Gardena-UPS4 | Smart-UPS 750 | AS2109142553 | v1.3.3.1 | 10.57.170.149 | RBG Gardena | 63.02 | 2021-03 | 2021-03 | 23.75 | RBC123 | 30.7 | 31.8 |  | 2026-09-16 | 2026-09-16
GLCCD-MadisonWindsor-UPS-SD1 | Smart-UPS SRT 1500 | AS2235191879 | v2.0.0.6 | 10.28.228.23 | GLCCD Madison | 63.06 | 2022-08 | 2022-08 | 24.99 | APCRBC155 | 53.21 | 55.9 |  | 2026-12-19 | 2027-05-25
GLCCD-Caledonia-IDF1-UPS4 | Smart-UPS 750 | AS2047141600 | v1.1.0.16 | 10.58.10.57 | GLCCD Caledonia | 63.08 | 2020-11 | 2020-11 | 19.34 | RBC123 | 76.44 | 78.6 |  | 2026-02-06 | 2026-02-06
RCCB-WestDundee-UPS-IDF6 | Smart-UPS 750 | AS2322133677 | v2.0.0.6 | 10.58.156.243 | RCCB West Dundee | 63.3 | 2023-06 | 2023-09 | 32.99 | APCRBC123 | 61.78 | 64.4 | Lower the battery temperature to 25 degrees C
GLCCD-AlsipDC-UPS-SW4-WH-Office | Smart-UPS 1500 | AS2303165903 | v2.0.0.6 | 10.20.144.186 | GLCCD Alsip | 63.48 | 2023-01 | 2023-04 | 30.19 | APCRBC133 | 35.31 | 36.4 | Lower the battery temperature to 25 degrees C | 2027-01-03 | 2028-03-19
MBUS-Roanoke-MDF-UPS1 | Smart-UPS SRT 1500 | AS2129192783 | v1.3.3.1 | 10.53.96.23 | MBUS Roanoke-TX | 63.71 | 2021-07 | 2021-07 | 21.1 | APCRBC155 | 27.07 | 28.4 |  | 2026-02-17 | 2026-02-17
mbcan-montreal-ups1 | Smart-UPS SRT 1500 | AS2137192338 | v1.3.3.1 | 10.44.48.23 | MBCAN Montreal | 64.04 | 2021-09 | 2021-09 | 22 | APCRBC155 | 0 | 0 |  | 2026-04-21 | 2026-04-21
GLCCD-AlsipDC-UPS-MDF-DMARK | Smart-UPS 750 | AS2122214836 | v1.3.3.1 | 10.20.144.230 | GLCCD Alsip | 64.04 | 2021-06 | 2021-06 | 23.53 | RBC123 | 55.8 | 57.2 |  | 2026-02-24 | 2026-02-24
GLCCD-AlsipPR-UPS-SW2-QA | Smart-UPS 750 | AS2110233474 | v1.3.3.1 | 10.45.243.120 | GLCCD Alsip | 64.12 | 2021-03 | 2021-03 | 23.43 | RBC123 | 42.72 | 43.5 |  | 2026-07-16 | 2026-08-21
MBUS-Whitewater-IDF2-UPS | Smart-UPS 1500 | AS2303232019 | v2.0.0.6 | 10.50.122.146 | MBUS Whitewater | 64.13 | 2023-01 | 2023-04 | 29.65 | APCRBC133 | 29.03 | 29.9 | Lower the battery temperature to 25 degrees C | 2026-11-03 | 2028-01-17
MBUS-Lexington-MDF-UPS2 | Smart-UPS SRT 1500 | AS2234293815 | v2.0.0.6 | 10.50.48.24 | MBUS Lexington | 64.18 | 2022-08 | 2022-08 | 21 | APCRBC155 | 7.09 | 10 |  | 2024-11-21 | 2024-11-21
apc75C84F | Smart-UPS X 3000 | AS2240154600 | v2.0.0.6 | 172.16.233.145 | RH Rosemont 9th Floor | 64.4 | 2022-10 | 2022-11 | 26.39 | APCRBC143 | 16.92 | 17.6 | Lower the battery temperature to 25 degrees C | 2027-03-05 | 2028-01-17
GLCCD-Lansing-UPS-SD1 | Smart-UPS SRT 1500 | AS2128290919 | v1.3.3.1 | 10.44.144.23 | GLCCD Lansing | 64.42 | 2021-07 | 2021-07 | 20.97 | APCRBC155 | 0 | 0 |  | 2026-01-14 | 2026-01-14
GLCCD-Niles-UPS-SW7-QA | Smart-UPS 750 | AS1829144761 | v7.1.2 | 10.44.2.208 | GLCCD Niles | 64.42 | 2018-07 | 2023-07 | 24.44 | RBC123 | 33.47 | 35.1 | Lower the battery temperature to 25 degrees C | 2028-08-20 | 2028-11-18
GLCCD-Caledonia-IDF2-UPS5 | Smart-UPS 750 | AS2047141597 | v1.1.0.16 | 10.58.10.15 | GLCCD Caledonia | 64.46 | 2020-11 | 2021-05 | 22.54 | RBC123 | 57.68 | 59.8 |  | 2026-08-07 | 2026-08-07
RCCB-ORANGE-UPS-SD1 | Smart-UPS SRT 1500 | AS2234293817 | v2.0.0.6 | 10.48.48.23 | RCCB Orange | 64.51 | 2022-08 | 2022-08 | 24.63 | APCRBC155 | 32.13 | 35.4 |  | 2027-05-07 | 2027-05-07
RCCB-VENTURA-UPS-SD2 | Smart-UPS SRT 1500 | AS2234293818 | v2.0.0.6 | 10.49.96.24 | RCCB Ventura | 64.56 | 2022-08 | 2022-08 | 24.72 | APCRBC155 | 0 | 0 |  | 2027-03-23 | 2027-03-23
MBUS-Coatsville-MDF-UPS2 | Smart-UPS SRT 1500 | AS2129292958 | v1.3.3.1 | 10.52.160.23 | MBUS Coatesville | 64.56 | 2021-07 | 2021-07 | 20.89 | APCRBC155 | 68.28 | 77.5 |  | 2026-01-27 | 2026-01-27
MBUS-Phoenix-IDF5-UPS | Smart-UPS 1000 | N12303141760 | v2.0.0.6 | 10.50.90.243 | MBUS Phoenix | 64.57 | 2023-01 | 2023-04 | 29.82 | APCRBC132 | 13.6 | 14.1 | Lower the battery temperature to 25 degrees C | 2026-08-26 | 2028-01-28
RCCB-LOS-ANGELES-UPS-SD1 | Smart-UPS SRT 1500 | AS2122393553 | v1.3.3.1 | 10.47.208.7 | RCCB Los Angeles | 64.64 | 2021-06 | 2021-06 | 21.84 | APCRBC155 | 0 | 0 |  | 2027-02-08 | 2027-02-08
MBUS-Pompano3PL-MDF-UPS2 | Smart-UPS SRT 1500 | AS2322192688 | v2.0.0.6 | 10.61.98.85 | MBUS Pompano | 64.89 | 2023-06 | 2023-06 | 26.92 | APCRBC155 | 15.01 | 15.9 | Lower the battery temperature to 25 degrees C | 2027-08-20 | 2028-01-08
apc7FE376 | Smart-UPS 1500 | AS2307154000 | v2.0.0.6 | 10.49.216.116 | RH West Palm Beach | 64.92 | 2023-02 | 2023-05 | 31 | APCRBC133 | 27.64 | 29.1 | Lower the battery temperature to 25 degrees C | 2028-06-29 | 2028-07-18
RCCB-BAKERSFIELD-UPS-SD1 | Smart-UPS SRT 1500 | AS2122194850 | v1.3.3.1 | 10.47.16.23 | RCCB Bakersfield | 65.05 | 2021-06 | 2021-06 | 21.25 | APCRBC155 | 0 | 0 |  | 2026-12-16 | 2026-12-16
MBUS-MasonCity-MDF-UPS3 | Smart-UPS 2200 | AS2323253829 | v2.0.0.6 | 10.53.95.59 | MBUS Mason City | 65.09 | 2023-06 | 2023-06 | 26.66 | RBC43 | 11.5 | 33.1 | Lower the battery temperature to 25 degrees C | 2028-04-29 | 2028-12-18
MBUS-Enfield-MDF-UPS2 | Smart-UPS SRT 1500 | AS2128290902 | v1.3.3.1 | 10.45.0.24 | MBUS Enfield | 65.27 | 2021-07 | 2021-07 | 22 | APCRBC155 | 30.66 | 51.4 |  | 2027-03-27 | 2027-03-27
apc4F446F | Smart-UPS 3000 | AS2115265939 | v1.3.3.1 | 10.47.210.163 | RCCB Los Angeles | 65.29 | 2021-04 | 2021-04 | 18.3 | RBC43 | 18.3 | 18.8
apc6F61C5 | Smart-UPS 2200 | AS2216265960 | v2.0.0.6 | 10.47.138.254 |  | 65.43 | 2022-04 | 2023-06 | 24.37 | RBC43 | 23.56 | 24.8
GLCCD-EAGAN-UPS-SW10-Guard | Smart-UPS 750 | AS2304230111 | v2.0.0.6 | 10.20.206.194 | GLCCD Eagan | 65.44 | 2023-01 | 2023-04 | 30.45 | APCRBC123 | 12.98 | 13.6 | Lower the battery temperature to 25 degrees C | 2026-01-28 | 2026-09-06
MBUS-Dickson-MDF-UPS2 | Smart-UPS SRT 1500 | AS2128290907 | v1.3.3.1 | 10.28.16.24 | MBUS Dickson | 65.62 | 2021-07 | 2021-07 | 20.39 | APCRBC155 | 0 | 0 |  | 2026-04-26 | 2026-04-26
apc59BAC1 | Smart-UPS 750 | AS2135261788 | v1.3.3.1 | 10.57.202.151 | RBG San Diego | 65.64 | 2021-09 | 2021-09 | 24.09 | RBC123 | 85.55 | 87.1 |  | 2026-06-16 | 2026-06-16
RBD-ChicagoHQ-MDFUPS1 | Smart-UPS SRT 1500 | AS2132290989 | v1.3.3.1 | 10.57.155.147 | RBG Chicago-HQ | 65.65 | 2021-08 | 2021-08 | 22.01 | APCRBC155 | 15.69 | 16.7 |  | 2027-03-28 | 2027-03-28
RCCB-WestDundee-UPS-IDF4 | Smart-UPS 750 | AS2322133706 | v2.0.0.6 | 10.58.156.157 | RCCB West Dundee | 65.85 | 2023-06 | 2023-10 | 32.15 | APCRBC123 | 65.88 | 66.4 | Lower the battery temperature to 25 degrees C
GLCCD-Tullahoma-HQ-UPS-SD1 | Smart-UPS SRT 1500 | AS2235191886 | v2.0.0.6 | 10.53.0.23 | GLCCD Tullahoma-PC | 65.93 | 2022-08 | 2022-08 | 24.21 | APCRBC155 | 25.65 | 28.3 |  | 2027-05-11 | 2027-05-14
GLCCD-Lansing-UPS-SD2 | Smart-UPS SRT 1500 | AS2128290916 | v1.3.3.1 | 10.44.144.24 | GLCCD Lansing | 66.13 | 2021-07 | 2021-07 | 21.76 | APCRBC155 | 56.12 | 57.9 |  | 2027-02-25 | 2027-02-25
GLCCD-Tullahoma-PC-UPS3 | Smart-UPS 750 | AS2137140230 | v1.3.3.1 | 10.53.2.46 | GLCCD Tullahoma-PC | 66.44 | 2021-09 | 2023-06 | 28.9 | RBC123 | 13.38 | 14.3 | Lower the battery temperature to 25 degrees C | 2027-06-08 | 2028-08-11
apc59BAB2 | Smart-UPS 750 | AS2135261784 | v1.3.3.1 | 10.57.202.57 | RBG San Diego | 66.47 | 2021-09 | 2021-09 | 25.51 | RBC123 | 70.42 | 71.5 | Lower the battery temperature to 25 degrees C | 2027-03-25 | 2027-03-30
RCCB-DOWNEY-UPS-SD1 | Smart-UPS SRT 1500 | AS2122393541 | v1.3.3.1 | 10.47.112.33 | RCCB Downey | 66.65 | 2021-06 | 2021-06 | 20.49 | APCRBC155 | 0.69 | 55.9 |  | 2025-12-05 | 2025-12-05
RCCB-WestDundee-UPS-MDF-Rack2 | Smart-UPS 3000 | AS2235154162 | v2.0.0.6 | 10.58.156.145 | RCCB West Dundee | 66.66 | 2022-09 | 2022-09 | 22.75 | RBC43 | 14.15 | 15
RCCB-Salinas-UPS-MDF | Smart-UPS 3000 | AS2230254522 | v2.0.0.6 | 10.48.195.68 | RCCB Salinas | 66.78 | 2022-07 | 2022-07 | 22.12 | RBC43 | 7.35 | 15 |  | 2027-11-03 | 2027-11-03
MBUS-Walker-MDF-UPS2 | Smart-UPS SRT 1500 | AS2108195656 | v1.3.3.1 | 10.44.96.14 | MBUS Walker | 66.82 | 2021-02 | 2021-02 | 18.3 | APCRBC155 | 37.56 | 39.5 |  | 2026-11-05 | 2026-11-05
GLCCD-VanBuren-UPS-MDF | Smart-UPS 1500 | AS2115231191 | v1.3.3.1 | 10.44.210.94 | GLCCD Van Buren | 66.88 | 2021-04 | 2021-04 | 18.29 | APCRBC133 | 19.53 | 20.1 |  | 2026-11-14 | 2026-11-14
MBUS-Dickson-MDF-UPS1 | Smart-UPS SRT 1500 | AS2128290906 | v1.3.3.1 | 10.28.16.23 | MBUS Dickson | 66.88 | 2021-07 | 2021-07 | 21.44 | APCRBC155 | 60.32 | 62 |  | 2027-03-05 | 2027-03-05
MBUS-CID-MDF-UPS2 | Smart-UPS SRT 1500 | AS2122194755 | v1.3.3.1 | 10.50.128.8 | MBUS City of Industry | 66.89 | 2021-06 | 2021-06 | 20.96 | APCRBC155 | 16.51 | 17.4 |  | 2027-02-01 | 2027-02-01
MBUS-Phoenix-XXX-UPS | Smart-UPS 750 | AS2136130031 | v1.3.3.1 | 10.50.90.241 | MBUS Phoenix | 66.94 | 2021-09 | 2021-09 | 23.19 | RBC123 | 88.06 | 98.8 |  | 2026-03-24 | 2026-03-24
MBUS-NorthLittleRock-IDF1-UPS | Smart-UPS 1500 | AS2307332122 | v2.0.0.6 | 172.16.12.185 | MBUS North Little Rock | 66.97 | 2023-02 | 2023-05 | 30.08 | APCRBC133 | 17.86 | 19.2 | Lower the battery temperature to 25 degrees C | 2026-12-27 | 2028-07-24
RCCB-WestDundee-UPS-MDF-Rack1 | Smart-UPS 3000 | AS2235154166 | v2.0.0.6 | 10.58.156.150 | RCCB West Dundee | 67.02 | 2022-09 | 2022-09 | 22.63 | RBC43 | 27.08 | 29.2
GLCCD-Niles-UPS-SW10-Jarvis | Smart-UPS 1500 | AS2307153176 | v2.0.0.6 | 10.44.2.201 | GLCCD Niles | 67.02 | 2023-02 | 2023-05 | 29.48 | APCRBC133 | 28.86 | 29.6 | Lower the battery temperature to 25 degrees C | 2027-04-09 | 2028-06-18
apc8AA65A | Smart-UPS 1500 | AS2341231526 | v2.0.0.6 | 10.45.26.146 | RBG Frederick | 67.03 | 2023-10 | 2024-01 | 31.9 | APCRBC133 | 23.81 | 25.7 | Lower the battery temperature to 25 degrees C
GLCCD-GrandRapids-UPS2 | SMART-UPS X1500 | AS2237162101 | v2.0.0.6 | 10.45.194.135 | GLCCD Grand Rapids | 67.24 | 2022-09 | 2022-12 | 26.81 | APCRBC115 | 7.8 | 13.9 | Lower the battery temperature to 25 degrees C | 2027-09-01 | 2028-03-24
apc6B7FBD | Smart-UPS 750 | 3S2228X10010 | v2.0.0.6 | 10.54.250.172 | RBG Austin | 67.3 | 2022-07 | 2022-10 | 28.28 | APCRBC123 | 28.84 | 41.4 | Lower the battery temperature to 25 degrees C | 2026-06-11 | 2027-01-11
MBUS-Roanoke-MDF-UPS2 | Smart-UPS SRT 1500 | AS2129292954 | v1.3.3.1 | 10.53.96.24 | MBUS Roanoke-TX | 67.41 | 2021-07 | 2021-07 | 21.14 | APCRBC155 | 42.55 | 51.8 |  | 2027-02-07 | 2027-02-07
apc6511BC | Smart-UPS 750 | 3S2227X16552 | v1.5.1.1 | 10.54.178.242 | RBG Nashville 301 | 67.6 | 2022-07 | 2022-10 | 28.37 | APCRBC123 | 14.03 | 14.8 | Lower the battery temperature to 25 degrees C | 2026-12-23 | 2027-11-04
MBUS-Atlanta-MDF-UPS4 | Smart-UPS 2200 | AS2204263481 | v1.3.3.1 | 10.240.109.229 | MBUS Atlanta | 67.65 | 2022-01 | 2022-01 | 19.84 | RBC43 | 24.11 | 24.7 |  | 2026-09-21 | 2026-09-21
RCCB-WestDundee-UPS-IDF3 | Smart-UPS 750 | AS2322133686 | v2.0.0.6 | 10.58.156.62 | RCCB West Dundee | 67.71 | 2023-06 | 2023-10 | 31.16 | APCRBC123 | 49.11 | 49.4 | Lower the battery temperature to 25 degrees C
GLCCD-EAGAN-UPS-SW1A-IDF1 | Smart-UPS 750 | AS2304230109 | v2.0.0.6 | 10.27.206.58 | GLCCD Eagan | 67.77 | 2023-01 | 2024-01 | 31.57 | APCRBC123 | 35.33 | 37.6 | Lower the battery temperature to 25 degrees C | 2026-03-30 | 2027-05-07
apc64CB90 | Smart-UPS SRT 1500 | AS2126292186 | v1.5.1.1 | 10.54.27.242 | RBG Orion | 67.97 | 2021-07 | 2021-07 | 20.83 | APCRBC155 | 35.73 | 38.7 |  | 2027-02-24 | 2027-02-24
GLCCD-Milwaukee-UPS-SW8 | Smart-UPS 3000 | AS2115271525 | v1.3.3.1 | 10.20.218.228 | GLCCD Milwaukee | 68.14 | 2021-04 | 2022-01 | 18.22 | RBC43 | 8 | 9.1 |  | 2027-07-01 | 2027-07-01
MBUS-Harriman-MDF-UPS2 | Smart-UPS SRT 1500 | AS2128290914 | v1.3.3.1 | 10.50.224.24 | MBUS Harriman | 68.73 | 2021-07 | 2021-07 | 20.74 | APCRBC155 | 0 | 0 |  | 2027-03-25 | 2027-03-25
RCCB-BISHOP-UPS | Smart-UPS 3000 | AS2115266039 | v1.3.3.1 | 10.47.59.254 | RCCB Bishop | 68.83 | 2021-04 | 2024-02 | 22.21 | RBC43 | 7.9 | 8 |  | 2029-09-13 | 2029-09-13
apc7488FD | Smart-UPS SRT 1500 | AS2234293707 | v2.0.0.6 | 10.56.42.59 | RBG Kona | 68.96 | 2022-08 | 2022-08 | 22.29 | APCRBC155 | 5.37 | 5.7 |  | 2026-02-06 | 2026-02-06
GLCCD-MadisonWindsor-UPS-SD2 | Smart-UPS SRT 1500 | AS2235191889 | v2.0.0.6 | 10.28.228.24 | GLCCD Madison | 69.13 | 2022-08 | 2022-08 | 24 | APCRBC155 | 0 | 0 |  | 2027-11-21 | 2028-04-23
MBUS-McCook-IDF2-UPS | SMART-UPS X1000 | AS2228160170 | v2.0.0.6 | 10.50.10.86 | MBUS McCook | 69.14 | 2022-07 | 2022-10 | 25.29 | APCRBC116 | 70.05 | 74 | Lower the battery temperature to 25 degrees C | 2028-04-30 | 2028-07-01
RCCB-ORANGE-UPS-MDF | Smart-UPS 2200 | AS2123162533 | v1.3.3.1 | 10.48.51.228 | RCCB Orange | 69.18 | 2021-06 | 2023-06 | 21.53 | RBC43 | 24.8 | 29.2 |  | 2029-03-04 | 2029-03-04
apc59BA98 | Smart-UPS 750 | AS2135261789 | v1.3.3.1 | 10.57.194.129 | RBG San Diego | 69.29 | 2021-09 | 2021-09 | 24.07 | RBC123 | 71.38 | 72.8 |  | 2027-06-02 | 2027-06-02
MBUS-Coatsville-MDF-UPS1 | Smart-UPS SRT 1500 | AS2129292957 | v1.3.3.1 | 10.52.160.24 | MBUS Coatesville | 69.32 | 2021-07 | 2021-07 | 20.2 | APCRBC155 | 0 | 0 |  | 2027-03-11 | 2027-03-11
apc59D9B1 | Smart-UPS SRT 1500 | AS2203394751 | v1.3.3.1 | 10.56.202.152 | RBG Kissimmee | 69.47 | 2022-01 | 2022-01 | 21.47 | APCRBC155 | 23.98 | 24.7 |  | 2027-03-20 | 2027-03-20
MBCAN-Brampton-UPS2 | Smart-UPS SRT 1500 | AS2137192333 | v1.3.3.1 | 10.28.128.24 | MBCAN Brampton | 69.51 | 2021-09 | 2021-09 | 21 | APCRBC155 | 24.33 | 42 |  | 2027-05-05 | 2027-05-05
RCCB-Fresno-UPS-MDF-Rack1-Bot | Smart-UPS 2200 | AS2123162531 | v1.3.3.1 | 10.47.170.58 | RCCB Fresno | 69.51 | 2021-06 | 2021-06 | 16.7 | RBC43 | 9.75 | 10.4
GLCCD-GrandRapids-UPS | SMART-UPS X1500 | AS2237162103 | v2.0.0.6 | 10.45.202.252 | GLCCD Grand Rapids | 69.54 | 2022-09 | 2023-06 | 27.01 | APCRBC115 | 0 | 0 | Lower the battery temperature to 25 degrees C | 2028-06-29 | 2028-12-05
GLCCD-Milwaukee-UPS-SW8-228 | Smart-UPS 3000 | AS2115271527 | v1.3.3.1 | 10.20.219.227 | GLCCD Milwaukee | 69.89 | 2021-04 | 2022-01 | 17.29 | RBC43 | 5.29 | 7 |  | 2027-07-16 | 2027-07-16
RCCB-Fresno-UPS-MDF-Rack1-Top | Smart-UPS 2200 | AS2122337950 | v1.3.3.1 | 10.47.171.18 | RCCB Fresno | 69.94 | 2021-06 | 2021-06 | 16.07 | RBC43 | 17.51 | 18.2
RCCB-Wrightstown-UPS-MDF-Rack | Smart-UPS 3000 | AS2237258274 | v2.0.0.6 | 10.28.230.86 | GLCCD Wrightstown | 70.12 | 2022-09 | 2022-09 | 21.65 | RBC43 | 4.02 | 5 |  | 2028-05-20 | 2028-05-20
apc59BABF | Smart-UPS 750 | AS2135261780 | v1.3.3.1 | 10.57.194.146 | RBG San Diego | 70.31 | 2021-09 | 2021-09 | 23.29 | RBC123 | 71.19 | 72.1 |  | 2027-05-28 | 2027-05-28
RCCB-SALINAS-UPS-SD2 | Smart-UPS SRT 1500 | AS2234293819 | v2.0.0.6 | 10.48.192.24 | RCCB Salinas | 70.36 | 2022-08 | 2022-08 | 23.19 | APCRBC155 | 24.93 | 26.1 |  | 2026-12-08 | 2026-12-08
MBUS-Walker-IDF1-UPS1 | Smart-UPS 1500 | AS2307153153 | v2.0.0.6 | 10.44.106.144 | MBUS Walker | 70.38 | 2023-02 | 2024-01 | 30.06 | APCRBC133 | 45.51 | 47 | Lower the battery temperature to 25 degrees C | 2027-07-15 | 2029-02-09
apc6511B9 | Smart-UPS 750 | 3S2205X12351 | v1.5.1.1 | 10.54.250.51 | RBG Austin | 70.39 | 2022-02 | 2022-05 | 25.11 | APCRBC123 | 24.47 | 25.1 | Lower the battery temperature to 25 degrees C | 2026-07-21 | 2026-07-30
mbcan-montreal-ups2 | Smart-UPS SRT 1500 | AS2137192332 | v1.3.3.1 | 10.44.48.24 | MBCAN Montreal | 70.41 | 2021-09 | 2021-09 | 20.74 | APCRBC155 | 33.26 | 34.6 |  | 2027-05-01 | 2027-05-01
apc5DF563 | Smart-UPS SRT 1500 | AS2147191325 | v1.3.3.1 | 10.57.194.59 | RBG San Diego | 70.47 | 2021-11 | 2021-11 | 19.96 | APCRBC155 | 37.95 | 39.2 |  | 2026-06-13 | 2026-06-13
MBUS-Pompano-MDF-UPS1 | Smart-UPS 2200 | AS2204263491 | v1.3.3.1 | 172.16.14.168 | MBUS Pompano | 70.53 | 2022-01 | 2022-01 | 19.39 | RBC43 | 14.53 | 16.2 |  | 2027-08-03 | 2027-08-03
RCCB-ORANGE-UPS-SD2 | Smart-UPS SRT 1500 | AS2234293822 | v2.0.0.6 | 10.48.48.24 | RCCB Orange | 70.71 | 2022-08 | 2022-08 | 23.44 | APCRBC155 | 0 | 0
GLCCD-Niles-UPS-MRC-2ndFl | Smart-UPS 3000 | AS2242155591 | v2.0.0.6 | 10.44.2.124 | GLCCD Niles | 70.72 | 2022-10 | 2022-10 | 21.58 | RBC43 | 11.37 | 12.3 |  | 2028-02-08 | 2028-02-08
apc6FCEDF | Smart-UPS SRT 1500 | AS2218291982 | v2.0.0.6 | 10.54.194.146 | RBG Jackson | 71.03 | 2022-05 | 2022-05 | 22.92 | APCRBC155 | 25.66 | 26.3 |  | 2027-12-21 | 2027-12-21
apc59A543 | Smart-UPS 750 | AS2135261782 | v1.3.3.1 | 10.57.194.153 | RBG San Diego | 71.25 | 2021-09 | 2021-09 | 22.24 | RBC123 | 82.87 | 84.5 |  | 2027-05-06 | 2027-05-06
GLCCD-EAGAN-UPS-NVR | Smart-UPS 1000 | 3S2152X10266 |  | 10.20.206.193 | GLCCD Eagan | 71.29 | 2021-12 | 2022-03 | 24.65 |  |  |  | Lower the battery temperature to 25 degrees C | 2027-07-23 | 2027-07-26
GLCCD-Niles-UPS-MDF-Rack4-Top | Smart-UPS 3000 | AS2237258272 | v2.0.0.6 | 10.44.2.178 | GLCCD Niles | 71.53 | 2022-09 | 2022-09 | 20.75 | RBC43 | 31.45 | 35.1 |  | 2028-02-27 | 2028-02-27
MBUS-Roanoke-IDF4-UPS | Smart-UPS 1500 | AS2307331941 | v2.0.0.6 | 10.240.40.81 | MBUS Roanoke-TX | 71.58 | 2023-02 | 2023-10 | 29.27 | APCRBC133 | 26.66 | 27.6 | Lower the battery temperature to 25 degrees C | 2027-04-28 | 2028-12-31
MBUS-Lexington-MDF-UPS1 | Smart-UPS SRT 1500 | AS2234293814 | v2.0.0.6 | 10.50.48.23 | MBUS Lexington | 71.76 | 2022-08 | 2022-08 | 22.99 | APCRBC155 | 46.32 | 48.3 |  | 2027-03-24 | 2027-03-24
MBUS-CID-IDF5-UPS | Smart-UPS 2200 | AS2328132460 | v2.0.0.6 | 10.50.138.241 | MBUS City of Industry | 71.8 | 2023-07 | 2023-07 | 24.05 | RBC43 | 18.77 | 18.9 |  | 2029-04-11 | 2029-04-11
apc7488E7 | Smart-UPS SRT 1500 | AS2234293713 | v2.0.0.6 | 10.56.42.56 | RBG Kona | 72.21 | 2022-08 | 2022-08 | 23.09 | APCRBC155 | 15.8 | 24 |  | 2028-03-11 | 2028-03-11
MBUS-Orlando-MDF-UPS3 | Smart-UPS 2200 | AS2325331371 | v2.0.0.6 | 172.16.27.145 | MBUS Orlando | 72.27 | 2023-06 | 2023-06 | 23.44 | RBC43 | 0 | 0 |  | 2029-02-07 | 2029-02-07
MBUS-McCook-IDF3-UPS | SMART-UPS X1000 | AS2228160163 | v2.0.0.6 | 10.50.10.114 | MBUS McCook | 72.31 | 2022-07 | 2022-10 | 24.18 | APCRBC116 | 67.87 | 71.3 | Lower the battery temperature to 25 degrees C | 2028-03-26 | 2028-07-03
MBUS-Portland-MDF-UPS1 | Smart-UPS 2200 | AS2325331350 | v2.0.0.6 | 10.50.26.196 | MBUS Portland | 72.49 | 2023-06 | 2023-06 | 23.43 | RBC43 | 63.17 | 76 |  | 2029-02-14 | 2029-02-16
GLCCD-Niles-UPS-SW5-HQ3rdFl | Smart-UPS 1500 | AS2307153183 | v2.0.0.6 | 10.44.3.72 | GLCCD Niles | 72.55 | 2023-02 | 2023-05 | 27.2 | APCRBC133 | 31.39 | 33.7 | Lower the battery temperature to 25 degrees C | 2027-08-20 | 2028-05-29
RCCB-Redding-UPS-MDF | Smart-UPS 2200 | AS2337361882 | v2.0.0.6 | 10.48.107.254 | RCCB Redding | 72.56 | 2023-09 | 2023-09 | 24.09 | RBC43 | 16.21 | 18.9 |  | 2028-11-08 | 2028-12-20
GLCCD-Tullahoma-HQ-UPS-SD2 | Smart-UPS SRT 1500 | AS2235191884 | v2.0.0.6 | 10.53.0.24 | GLCCD Tullahoma-PC | 72.87 | 2022-08 | 2022-08 | 23.14 | APCRBC155 | 26.08 | 30 |  | 2028-05-04 | 2028-05-04
GLCCD-GrandRapids-UPS | SMART-UPS X1500 | AS2237162102 | v2.0.0.6 | 10.45.202.250 | GLCCD Grand Rapids | 72.94 | 2022-09 | 2023-06 | 26.12 | APCRBC115 | 10.87 | 13 | Lower the battery temperature to 25 degrees C | 2028-10-15 | 2029-03-17
apc54682A | Smart-UPS 750 | 3S2204X10257 | v7.1.2 | 192.168.70.154 | MBCAN Calgary | 73.1 | 2022-01 | 2022-04 | 24.6 | APCRBC123 | 30.12 | 31.6 | Lower the battery temperature to 25 degrees C | 2027-08-01 | 2027-08-12
RCCB-LOS-ANGELES-UPS-Rack7 | Smart-UPS 3000 | AS2230254516 | v2.0.0.6 | 10.47.210.214 | RCCB Los Angeles | 73.22 | 2022-07 | 2022-07 | 19.9 | RBC43 | 28 | 30.6 |  | 2027-05-16 | 2027-05-16
apc6511C4 | Smart-UPS 750 | 3S2227X16483 | v1.5.1.1 | 10.54.250.61 | RBG Austin | 73.28 | 2022-07 | 2022-10 | 26.05 | APCRBC123 | 83.64 | 84.8 | Lower the battery temperature to 25 degrees C | 2026-04-05 | 2026-06-11
RCCB-SALINAS-UPS-SD1 | Smart-UPS SRT 1500 | AS2234293816 | v2.0.0.6 | 10.48.192.23 | RCCB Salinas | 73.49 | 2022-08 | 2022-08 | 22.37 | APCRBC155 | 0 | 0 |  | 2027-04-15 | 2027-04-15
apc74881F | Smart-UPS SRT 1500 | AS2235191883 | v2.0.0.6 | 10.47.32.24 | RCCB Benicia | 73.53 | 2022-08 | 2022-08 | 23 | APCRBC155 | 61.22 | 62.3
MBUS-MasonCity-IDF1-UPS | Smart-UPS 1000 | 3S2225X10997 | v2.0.0.6 | 10.53.95.146 | MBUS Mason City | 73.86 | 2022-06 | 2022-08 | 25.83 | APCRBC132 | 18.08 | 18.8 | Lower the battery temperature to 25 degrees C | 2027-12-12 | 2028-01-03
RCCB-Fontana-UPS-MDF1 | Smart-UPS 3000 | AS2235253800 | v2.0.0.6 | 10.58.140.58 | RCCB Victorville | 73.94 | 2022-09 | 2022-09 | 20.44 | RBC43 | 23.86 | 25.3
RCCB-SanJose-UPS-SD1 | Smart-UPS SRT 1500 | AS2235191880 | v2.0.0.6 | 10.48.144.23 | RCCB San Jose | 74.09 | 2022-08 | 2022-08 | 22.05 | APCRBC155 | 45.6 | 47.4 |  | 2027-05-07 | 2027-05-07
RCCB-BENICIA-UPS-NVR | SMART-UPS X1500 | AS2237353137 | v2.0.0.6 | 10.47.43.254 |  | 74.11 | 2022-09 | 2022-12 | 25.01 | APCRBC115 | 8.77 | 10 | Lower the battery temperature to 25 degrees C
MBUS-Lebanon-IDF2-UPS1 | Smart-UPS 1000 | 3S2321X13267 | v2.0.0.6 | 10.50.74.248 | MBUS Lebanon | 74.22 | 2023-05 | 2023-08 | 28.46 | APCRBC132 | 44.35 | 45.8 | Lower the battery temperature to 25 degrees C | 2027-08-26 | 2028-08-12
RCCB-Wrightstown-UPS-sd2 | Smart-UPS SRT 1500 | AS2319293074 | v2.0.0.6 | 10.28.230.24 | GLCCD Wrightstown | 74.89 | 2023-05 | 2023-05 | 24 | APCRBC155 | 30.03 | 31.6 |  | 2027-12-24 | 2027-12-24
RCCB-WestDundee-UPS-IDF2 | Smart-UPS 750 | AS2322133673 | v2.0.0.6 | 10.58.156.245 | RCCB West Dundee | 74.99 | 2023-06 | 2023-10 | 28.9 | APCRBC123 | 56.92 | 57.2 | Lower the battery temperature to 25 degrees C
MBUS-NorthLittleRock-MDF-UPS1 | Smart-UPS 2200 | AS2323253981 | v2.0.0.6 | 172.16.12.171 | MBUS North Little Rock | 75.05 | 2023-06 | 2023-06 | 22.36 | RBC43 | 28.72 | 35.8 |  | 2028-02-06 | 2028-02-24
MBUS-Fairfield-IDF2-UPS1 | Smart-UPS 1000 | 3S2321X13270 | v2.0.0.6 | 10.240.56.146 | MBUS Fairfield | 75.06 | 2023-05 | 2023-08 | 28.65 | APCRBC132 | 31.34 | 31.8 | Lower the battery temperature to 25 degrees C | 2027-10-02 | 2028-12-20
MBUS-Whitewater-MDF-UPS1 | Smart-UPS 3000 | AS2242162498 | v2.0.0.6 | 10.50.122.219 | MBUS Whitewater | 75.17 | 2022-10 | 2022-10 | 18.91 | RBC43 | 49.14 | 54.7 |  | 2025-12-31 | 2025-12-31
GLCCD-EAGAN-UPS-SW7-CashOffice | Smart-UPS 3000 | AS2132164669 | v2.0.0.6 | 10.27.206.144 | GLCCD Eagan | 75.37 | 2022-03 | 2024-02 | 21.67 | RBC43 | 22.01 | 22.8 |  | 2028-01-28 | 2028-01-28
apc7A48AC | Smart-UPS 750 | 3S2321X17243 | v2.0.0.6 | 192.168.40.136 | MBCAN Montreal | 75.58 | 2023-05 | 2023-08 | 28.83 | APCRBC123 | 41.02 | 41.6 | Lower the battery temperature to 25 degrees C | 2027-02-18 | 2028-07-15
apc6511A0 | Smart-UPS 750 | 3S2227X16481 | v1.5.1.1 | 10.54.250.147 | RBG Austin | 75.71 | 2022-07 | 2022-10 | 24.83 | APCRBC123 | 37.47 | 38.7 | Lower the battery temperature to 25 degrees C | 2026-10-04 | 2026-11-20
MBUS-Lexington-IDF2-UPS2 | Smart-UPS 1500 | AS2323160159 | v2.0.0.6 | 10.50.50.15 | MBUS Lexington | 75.9 | 2023-06 | 2023-09 | 27.66 | APCRBC133 | 21.26 | 22 | Lower the battery temperature to 25 degrees C | 2028-10-07 | 2029-01-13
GLCCD-Milwaukee-UPS-SWx-IDF1 | Smart-UPS 1500 | AS2303165866 | v2.0.0.6 | 10.20.218.115 | GLCCD Milwaukee | 76.01 | 2023-01 | 2023-04 | 24.98 | APCRBC133 | 36.22 | 37 | Lower the battery temperature to 25 degrees C | 2028-01-04 | 2028-03-13
MBUS-Stockton-IDF1-UPS1 | Smart-UPS 1500 | AS2307331922 | v2.0.0.6 | 172.16.24.232 | MBUS Stockton | 76.1 | 2023-02 | 2023-05 | 26.63 | APCRBC133 | 41.83 | 44.1 | Lower the battery temperature to 25 degrees C | 2028-07-26 | 2028-09-08
RCCB-Wrightstown-UPS-sd1 | Smart-UPS SRT 1500 | AS2319293076 | v2.0.0.6 | 10.28.230.23 | GLCCD Wrightstown | 76.25 | 2023-05 | 2023-05 | 24 | APCRBC155 | 24.96 | 26.1 |  | 2029-01-16 | 2029-01-16
MBUS-Fridley-IDF2-UPS | Smart-UPS 1000 | 3S2225X10999 | v2.0.0.6 | 10.28.117.146 | MBUS Fridley | 76.27 | 2022-06 | 2022-08 | 24.49 | APCRBC132 | 58.85 | 59.7 |  | 2027-08-29 | 2027-08-30
GLCCD-Milwaukee-UPS-SW9 | Smart-UPS 750 | AS2304230113 | v2.0.0.6 | 10.20.218.144 | GLCCD Milwaukee | 76.53 | 2023-01 | 2023-04 | 27.62 | APCRBC123 | 41.82 | 42.7 | Lower the battery temperature to 25 degrees C | 2027-11-09 | 2028-05-12
RCCB-SanJose-UPS-SD2 | Smart-UPS SRT 1500 | AS2235191890 | v2.0.0.6 | 10.48.144.24 | RCCB San Jose | 76.56 | 2022-08 | 2022-08 | 21.49 | APCRBC155 | 0 | 0 |  | 2027-04-16 | 2027-04-16
GLCCD-Niles-UPS-IDF.SW6 | Smart-UPS 750 | AS2322133636 | v2.0.0.6 | 10.44.2.196 | GLCCD Niles | 76.57 | 2023-06 | 2023-09 | 27.88 | APCRBC123 | 42.59 | 43.1 | Lower the battery temperature to 25 degrees C | 2027-08-27 | 2028-05-27
GLCCD-Niles-UPS-SW3-ProdWarRoom | Smart-UPS 2200 | AS2327261627 | v2.0.0.6 | 10.44.3.4 | GLCCD Niles | 76.85 | 2023-07 | 2023-07 | 22.23 | RBC43 | 13.06 | 14.3 |  | 2029-01-16 | 2029-01-16
GLCCD-Niles-UPS-SW9-DEPAL | Smart-UPS 750 | AS2304230184 | v2.0.0.6 | 10.44.2.182 | GLCCD Niles | 77.04 | 2023-01 | 2023-05 | 27.52 | APCRBC123 | 42.7 | 43.2 | Lower the battery temperature to 25 degrees C | 2027-12-19 | 2028-08-01
MBUS-Sumner-MDF-UPS2 | Smart-UPS SRT 5000 | AS2315272240 | v2.0.0.6 | 10.50.106.236 | MBUS Sumner | 77.12 | 2023-04 | 2023-09 | 23.07 | APCRBC140 | 24 | 24.9 |  | 2029-05-27 | 2029-05-27
MBUS-Garner-MDF-UPS2 | Smart-UPS SRT 1500 | AS2235191965 | v2.0.0.6 | 10.50.32.24 | MBUS Garner | 77.19 | 2022-08 | 2022-08 | 21 | APCRBC155 | 36.7 | 38 |  | 2027-02-14 | 2027-02-14
apc700102 | Smart-UPS SRT 1500 | AS2218291981 | v2.0.0.6 | 10.54.170.59 | RBG Nashville 245 | 77.35 | 2022-05 | 2022-05 | 20.72 | APCRBC155 | 42.95 | 44.2 |  | 2028-01-09 | 2028-01-09
MBUS-DicksonROP-IDF2-UPS1 | Smart-UPS 1000 | 3S2321X13263 | v2.0.0.6 | 10.28.111.147 | MBUS DicksonROP | 77.38 | 2023-05 | 2023-12 | 28.31 | APCRBC132 | 18.91 | 20 | Lower the battery temperature to 25 degrees C | 2028-01-06 | 2029-02-20
Coachella-UPS-MDF | Smart-UPS 2200 | AS2216265968 | v2.0.0.6 | 10.47.99.162 |  | 77.4 | 2022-04 | 2023-07 | 20.62 | RBC43 | 17.58 | 17.6
MBUS-Conroe-IDF1-UPS2 | Smart-UPS 1500 | AS2307134470 | v2.0.0.6 | 10.27.22.58 | MBUS Conroe | 77.45 | 2023-02 | 2023-11 | 27.14 | APCRBC133 | 26.11 | 26.8 | Lower the battery temperature to 25 degrees C | 2028-05-29 | 2029-03-14
RH-OFFICE-7N-SW1 | Smart-UPS X 3000 | AS2240154593 | v2.0.0.6 | 172.16.231.137 | RH Rosemont 7th Floor | 77.89 | 2022-10 | 2024-04 | 25.67 | APCRBC143 | 19.81 | 20.8 | Lower the battery temperature to 25 degrees C | 2029-08-07 | 2029-12-20
MBUS-Pompano-MDF-UPS2 | Smart-UPS 2200 | AS2323253827 | v2.0.0.6 | 172.16.14.184 | MBUS Pompano | 77.91 | 2023-06 | 2023-06 | 21.44 | RBC43 | 25.98 | 27.3 |  | 2028-12-22 | 2028-12-22
apc59BAC6 | Smart-UPS 750 | AS2135261786 | v1.3.3.1 | 10.57.194.121 | RBG San Diego | 78.01 | 2021-09 | 2023-02 | 23.54 | RBC123 | 50.42 | 51.3 |  | 2028-09-14 | 2028-09-14
MBUS-Enfield-IDF1-UPS1 | Smart-UPS 1500 | AS2307134546 | v2.0.0.6 | 172.16.11.175 | MBUS Enfield | 78.25 | 2023-02 | 2023-05 | 24.87 | APCRBC133 | 23.28 | 23.8 |  | 2028-03-02 | 2028-05-05
MBUS-Pompano3PL-MDF-UPS3 | Smart-UPS 750 | AS2137140218 | v1.3.3.1 | 10.61.98.196 | MBUS Pompano | 78.39 | 2021-09 | 2023-01 | 22.99 | RBC123 | 0 | 0 |  | 2028-10-13 | 2028-10-13
MBUS-CID-IDF7-UPS | Smart-UPS 2200 | AS2328132462 | v2.0.0.6 | 10.50.138.247 | MBUS City of Industry | 78.42 | 2023-07 | 2023-07 | 21.67 | RBC43 | 21.31 | 23.4 |  | 2028-12-30 | 2028-12-30
MBUS-Lebanon-MDF-UPS4 | Smart-UPS 1500 | AS2307154002 | v2.0.0.6 | 10.50.74.254 | MBUS Lebanon | 78.71 | 2023-02 | 2023-05 | 24.51 | APCRBC133 | 49.63 | 77.2 |  | 2027-08-08 | 2028-01-14
apc700126 | Smart-UPS SRT 1500 | AS2218291979 | v2.0.0.6 | 10.54.170.146 | RBG Nashville 245 | 78.79 | 2022-05 | 2022-05 | 19.78 | APCRBC155 | 24.56 | 25.2 |  | 2028-01-09 | 2028-01-09
MBUS-Atlanta-MDF-UPS3 | Smart-UPS 2200 | AS2323253869 | v2.0.0.6 | 10.20.109.93 | MBUS Atlanta | 78.85 | 2023-06 | 2023-06 | 21.22 | RBC43 | 13.92 | 14.3 |  | 2029-01-20 | 2029-01-20
MBUS-Lexington-IDF1-UPS2 | Smart-UPS 1000 | 3S2321X13357 | v2.0.0.6 | 10.50.48.107 | MBUS Lexington | 79.06 | 2023-05 | 2023-08 | 27.35 | APCRBC132 | 6.4 | 6.9 | Lower the battery temperature to 25 degrees C | 2028-04-21 | 2029-01-17
MBUS-DicksonROP-IDF3-UPS1 | Smart-UPS 1000 | 3S2321X13264 | v2.0.0.6 | 10.28.111.58 | MBUS DicksonROP | 79.64 | 2023-05 | 2023-12 | 27.62 | APCRBC132 | 15.79 | 16.3 | Lower the battery temperature to 25 degrees C | 2028-02-14 | 2029-03-20
MBUS-Garner-MDF-UPS1 | Smart-UPS SRT 1500 | AS2235292681 | v2.0.0.6 | 10.50.32.23 | MBUS Garner | 79.65 | 2022-08 | 2022-08 | 21 | APCRBC155 | 22.18 | 23.7 |  | 2028-03-07 | 2028-03-07
GLCCD-Lacrosse-UPS | Smart-UPS 2200 | AS2313152321 | v2.0.0.6 | 10.20.214.183 | GLCCD La Crosse | 79.81 | 2023-03 | 2023-03 | 20.26 | RBC43 | 12.93 | 13 |  | 2028-10-23 | 2028-10-23
GLCCD-Milwaukee-UPS-SW2-IDF2 | Smart-UPS 750 | AS2113162332 | v1.3.3.1 | 10.20.218.122 | GLCCD Milwaukee | 79.98 | 2021-04 | 2024-02 | 24.4 | RBC123 | 13.06 | 13.6 |  | 2029-01-05 | 2029-01-05
MBUS-Lebanon-MDF-UPS3 | Smart-UPS 1500 | AS2307154005 | v2.0.0.6 | 10.50.74.253 | MBUS Lebanon | 80.07 | 2023-02 | 2023-05 | 24.21 | APCRBC133 | 41.07 | 52.8 |  | 2028-01-14 | 2028-04-13
GLCCD-AlsipDC-UPS-MDF-NVR-Bottom | Smart-UPS 3000 | AS2237258276 | v2.0.0.6 | 10.20.144.229 | GLCCD Alsip | 80.34 | 2022-09 | 2023-08 | 20.06 | RBC43 | 15.7 | 19.6 |  | 2027-10-20 | 2027-10-20
MBUS-Lebanon-IDF1-UPS1 | Smart-UPS 1500 | AS2307154003 | v2.0.0.6 | 10.50.74.251 | MBUS Lebanon | 80.36 | 2023-02 | 2023-05 | 24.72 | APCRBC133 | 11.71 | 12.6 |  | 2028-09-09 | 2028-09-24
RCCB-Fontana-UPS-MDF2 | Smart-UPS 3000 | AS2235253795 | v2.0.0.6 | 10.58.140.147 | RCCB Victorville | 80.64 | 2022-09 | 2022-09 | 18.12 | RBC43 | 0 | 0
MBUS-Manassas-MDF-UPS4 | Smart-UPS 1500 | AS2307332126 | v2.0.0.6 | 10.50.250.147 | MBUS Manassas | 80.73 | 2023-02 | 2023-05 | 24.37 | APCRBC133 | 22.83 | 50.9 |  | 2028-03-24 | 2028-07-24
MBUS-Manassas-MDF-UPS3 | Smart-UPS 1500 | AS2307332121 | v2.0.0.6 | 10.50.250.146 | MBUS Manassas | 80.83 | 2023-02 | 2023-05 | 24.39 | APCRBC133 | 0 | 0 |  | 2028-06-15 | 2028-10-18
RCCB-LOS-ANGELES-UPS-SW5-Rack6 | SMART-UPS X1500 | AS2237353131 | v2.0.0.6 | 10.47.219.254 | RCCB Los Angeles | 80.85 | 2022-09 | 2022-12 | 22.69 | APCRBC115 | 18.6 | 19
MBUS-Lebanon-IDF3-UPS1 | Smart-UPS 1000 | 3S2321X13269 | v2.0.0.6 | 10.50.74.249 | MBUS Lebanon | 80.95 | 2023-05 | 2023-12 | 27.36 | APCRBC132 | 17.5 | 18 | Lower the battery temperature to 25 degrees C | 2028-10-01 | 2029-05-29
GLCCD-Caledonia-UPS-MDF | SMART-UPS X1500 | AS2237162112 | v2.0.0.6 | 10.58.10.12 | GLCCD Caledonia | 82.17 | 2022-09 | 2023-08 | 23.64 | APCRBC115 | 13.19 | 14.4 |  | 2029-03-08 | 2029-03-08
MBUS-Coatsville-IDF1-UPS1 | Smart-UPS 2200 | AS2324160004 | v2.0.0.6 | 10.20.54.156 | MBUS Coatesville | 82.19 | 2023-06 | 2023-06 | 20.34 | RBC43 | 14.26 | 14.3 |  | 2029-01-04 | 2029-01-04
apc86754D | Smart-UPS 750 | AS2322133678 | v2.0.0.6 | 172.16.30.153 | RBG Chantilly | 82.22 | 2023-06 | 2023-09 | 26.84 | APCRBC123 | 68.35 | 70 | Lower the battery temperature to 25 degrees C | 2028-01-12 | 2028-09-03
MBUS-Stockton-MDF-UPS1 | Smart-UPS 1500 | AS2307331928 | v2.0.0.6 | 172.16.24.220 | MBUS Stockton | 82.33 | 2023-02 | 2023-09 | 24.66 | APCRBC133 | 0 | 0 |  | 2029-03-03 | 2029-03-03
MBUS-StJohns-IDF4-UPS1 | Smart-UPS 1000 | 3S2224X16454 | v2.0.0.6 | 10.50.222.58 | MBUS St Johns | 82.47 | 2022-06 | 2022-09 | 14.3 | APCRBC132 | 66.77 | 67.3 |  | 2028-01-11 | 2028-01-11
MBUS-StJohns-IDF3-UPS1 | Smart-UPS 1000 | 3S2224X16475 | v2.0.0.6 | 10.50.222.147 | MBUS St Johns | 82.72 | 2022-06 | 2022-09 | 11.99 | APCRBC132 | 35.48 | 36 |  | 2028-02-08 | 2028-02-08
MBUS-Phoenix-IDF4-UPS | Smart-UPS 1000 | N12303141712 | v2.0.0.6 | 10.50.80.104 | MBUS Phoenix | 82.94 | 2023-01 | 2023-04 | 6.94 | APCRBC132 | 25.82 | 26.6 |  | 2028-09-05 | 2028-09-05
MBUS-Harriman-IDF1-UPS | Smart-UPS 1500 | AS2307332087 | v2.0.0.6 | 172.16.49.189 | MBUS Harriman | 83.14 | 2023-02 | 2023-05 | 22.86 | APCRBC133 | 24.51 | 24.9 |  | 2028-06-27 | 2028-08-28
GLCCD-EAGAN-UPS-SW3-CO2Fill | Smart-UPS 750 | AS2304230114 | v2.0.0.6 | 10.27.206.59 | GLCCD Eagan | 83.23 | 2023-01 | 2024-02 | 27.07 | APCRBC123 | 24.07 | 24.3 | Lower the battery temperature to 25 degrees C | 2028-12-27 | 2029-06-18
MBUS-Fairfield-IDF1-UPS | Smart-UPS 1500 | AS2307154009 | v2.0.0.6 | 10.240.56.58 | MBUS Fairfield | 83.34 | 2023-02 | 2023-05 | 22.86 | APCRBC133 | 32.81 | 33.2 |  | 2028-08-30 | 2028-08-30
MBUS-Orlando-MDF-UPS2 | Smart-UPS SRT 1500 | AS2351392750 | v6.8.2 | 10.50.144.23 | MBUS Orlando | 84.1 | 2023-12 | 2023-12 | 23.03 | APCRBC155 | 0 | 0 |  | 2029-06-16 | 2029-06-16
GLCCD-AlsipPR-UPS-MDF-Bottom | Smart-UPS 3000 | AS2237364614 | v2.0.0.6 | 10.45.243.228 | GLCCD Alsip | 84.25 | 2022-09 | 2023-08 | 18.6 | RBC43 | 27.98 | 30.6 |  | 2027-04-09 | 2027-04-09
RCCB-WestDundee-UPS-IDF5 | Smart-UPS 750 | AS2322133674 | v2.0.0.6 | 10.58.156.240 | RCCB West Dundee | 84.53 | 2023-06 | 2023-10 | 25.74 | APCRBC123 | 76.83 | 77.7 | Lower the battery temperature to 25 degrees C
MBUS-SaltLakeCity-MDF-UPS | Smart-UPS 3000 | AS2325160883 | v2.0.0.6 | 10.52.206.146 | MBUS Salt Lake City | 84.9 | 2023-06 | 2023-06 | 19.08 | RBC43 | 25.02 | 28 |  | 2027-12-19 | 2027-12-19
MBUS-CID-IDF6-UPS | Smart-UPS 750 | AS2136130061 | v1.3.3.1 | 10.50.138.243 | MBUS City of Industry | 85.2 | 2021-09 | 2023-12 | 8.5 | RBC123 | 50.9 | 51.3 |  | 2028-03-06 | 2028-03-06
apc867509 | Smart-UPS 750 | AS2322133617 | v2.0.0.6 | 10.27.76.180 | RBG Chantilly | 86.03 | 2023-06 | 2024-02 | 26.52 | APCRBC123 | 31.17 | 32.9 | Lower the battery temperature to 25 degrees C | 2028-08-20 | 2029-05-31
MBUS-Walker-MDF-UPS3 | Smart-UPS 1500 | AS2307153148 | v2.0.0.6 | 10.44.106.58 | MBUS Walker | 86.27 | 2023-02 | 2023-05 | 21.01 | APCRBC133 | 10.25 | 20.6 |  | 2028-10-23 | 2028-10-23
MBUS-Enfield-IDF2-UPS2 | Smart-UPS 1000 | 3S2316X12828 | v2.0.0.6 | 172.16.11.181 | MBUS Enfield | 86.6 | 2023-04 | 2023-07 | 23.79 | APCRBC132 | 8.19 | 8.4 | Lower the battery temperature to 25 degrees C | 2028-01-18 | 2028-11-24
MBUS-Harriman-IDF2-UPS | Smart-UPS 1000 | 3S2316X12964 | v2.0.0.6 | 172.16.49.181 | MBUS Harriman | 87.19 | 2023-04 | 2023-07 | 22.65 | APCRBC132 | 8.92 | 11.1 |  | 2028-09-25 | 2028-09-25
MBUS-Harriman-MDF-UPS4 | Smart-UPS 2200 | AS2324160009 | v2.0.0.6 | 172.16.49.185 | MBUS Harriman | 88.28 | 2023-06 | 2023-06 | 18.06 | RBC43 | 0.11 | 4 |  | 2029-03-11 | 2029-03-11
MBUS-Garner-MDF-UPS3 | Smart-UPS 1500 | AS2323160160 | v2.0.0.6 | 10.50.42.161 | MBUS Garner | 88.36 | 2023-06 | 2023-09 | 21.25 | APCRBC133 | 69.78 | 82 |  | 2028-10-23 | 2028-10-23
MBUS-Harriman-MDF-UPS5 | Smart-UPS 2200 | AS2323253890 | v2.0.0.6 | 172.16.49.169 | MBUS Harriman | 88.46 | 2023-06 | 2023-06 | 18 | RBC43 | 0 | 0 |  | 2029-03-10 | 2029-03-10
MBUS-Roanoke-IDF1-UPS | Smart-UPS 1500 | AS2307134472 | v2.0.0.6 | 10.240.40.200 | MBUS Roanoke-TX | 88.69 | 2023-02 | 2023-05 | 17.75 | APCRBC133 | 46.33 | 47 |  | 2028-07-17 | 2028-07-17
MBUS-Roanoke-MDF-UPS4 | Smart-UPS 3000 | AS2338154029 | v2.0.0.6 | 10.240.40.201 | MBUS Roanoke-TX | 89.01 | 2023-09 | 2023-09 | 17.95 | RBC43 | 26.31 | 98.1 |  | 2027-02-08 | 2027-02-08
MBUS-Roanoke-MDF-UPS3 | Smart-UPS 3000 | AS2338154032 | v2.0.0.6 | 10.240.40.86 | MBUS Roanoke-TX | 89.35 | 2023-09 | 2024-02 | 19.39 | RBC43 | 0 | 0 |  | 2029-02-21 | 2029-02-21
MBUS-Manassas-IDF1-UPS | Smart-UPS 1500 | AS2307332118 | v2.0.0.6 | 10.50.250.58 | MBUS Manassas | 89.37 | 2023-02 | 2023-05 | 12.9 | APCRBC133 | 48.16 | 48.7 |  | 2028-08-20 | 2028-08-20
MBUS-Atlanta-IDF1-UPS1 | Smart-UPS 1500 | AS2307134544 | v2.0.0.6 | 10.20.109.167 | MBUS Atlanta | 89.44 | 2023-02 | 2023-05 | 12.61 | APCRBC133 | 81.05 | 82.2 |  | 2028-06-18 | 2028-06-18
MBUS-Atlanta-IDF2-UPS1 | Smart-UPS 1500 | AS2307134545 | v2.0.0.6 | 10.20.109.199 | MBUS Atlanta | 89.46 | 2023-02 | 2023-05 | 12.49 | APCRBC133 | 81.97 | 89.3 |  | 2028-07-19 | 2028-07-19
MBUS-DicksonROP-IDF1-UPS | Smart-UPS 1000 | 3S2321X13278 | v2.0.0.6 | 172.16.13.140 | MBUS DicksonROP | 89.61 | 2023-05 | 2023-12 | 23.76 | APCRBC132 | 17.17 | 18.6 |  | 2029-03-23 | 2029-04-30
GLCCD-AlsipPR-UPS-MDF-Top | Smart-UPS 2200 | AS2345163665 | v2.0.0.6 | 10.45.242.99 | GLCCD Alsip | 89.83 | 2023-11 | 2023-11 | 18.53 | RBC43 | 42.71 | 49.4 |  | 2027-11-13 | 2027-11-13
MBUS-Portland-IDF1-UPS1 | Smart-UPS 1000 | 3S2312X10900 | v2.0.0.6 | 10.50.26.198 | MBUS Portland | 90.51 | 2023-03 | 2023-06 | 13.43 | APCRBC132 | 51.45 | 52 |  | 2028-10-20 | 2028-10-20
MBUS-Walker-IDF2-UPS1 | Smart-UPS 1500 | AS2307153150 | v2.0.0.6 | 10.44.106.147 | MBUS Walker | 90.58 | 2023-02 | 2024-01 | 7.65 | APCRBC133 | 37.6 | 39 |  | 2029-05-09 | 2029-05-09
MBUS-Roanoke-IDF2-UPS | Smart-UPS 1500 | AS2307134468 | v2.0.0.6 | 10.240.40.202 | MBUS Roanoke-TX | 91.79 | 2023-02 | 2023-10 | 16.3 | APCRBC133 | 43.75 | 44.1 |  | 2029-01-28 | 2029-01-28
MBUS-Roanoke-IDF3-UPS | Smart-UPS 1500 | AS2307331939 | v2.0.0.6 | 10.240.40.203 | MBUS Roanoke-TX | 92.04 | 2023-02 | 2023-10 | 15.08 | APCRBC133 | 39.32 | 39.8 |  | 2029-01-16 | 2029-01-16
apc8AA3EA | Smart-UPS 2200 | AS2340144619 | v2.0.0.6 | 10.45.26.147 | RBG Frederick | 92.66 | 2023-10 | 2024-05 | 18.84 | RBC43 | 7.53 | 18.2
2829863D10F6 | Smart-UPS 1000 | 3S2029X16956 |  | 10.45.146.89
GLCCD-ALPINA-UPS-MDF | Smart-UPS 1500 | AS2303165901 | v2.0.0.6 | 10.45.74.252 | GLCCD Alpena |  |  |  | 21.86 | APCRBC133 | 12.3 | 12.7 |  | 2028-09-21 | 2028-09-21
GLCCD-ALSIP-PR-UPS-MDF-Top | Smart-UPS 1500 | AS2046233153 | v1.1.0.16 | 10.45.243.125 | GLCCD Alsip |  |  |  | 20.1 | APCRBC133 |  |  |  | 2026-04-23 | 2026-04-23
GLCCD-AlsipDC-UPS-SW5-ExecCloset | Smart-UPS 750 | AS1740231596 | v6.5.0 | 10.20.145.107 | GLCCD Alsip |  |  |  | 24.6 | RBC123
GLCCD-AlsipPR-UPS-SW3-LOFT | Smart-UPS 750 | AS2102143528 | v1.3.3.1 | 10.45.243.123 | GLCCD Alsip |  |  |  | 22.44 | RBC123 |  |  |  | 2025-10-23 | 2025-11-01
GLCCD-BayCity-UPS-SW1-MDF | Smart-UPS 3000 | AS2237259021 | v2.0.0.6 | 10.45.146.228 | GLCCD Bay City |  |  |  | 22.9 | RBC43 | 33.48 | 50.8 |  | 2027-11-01 | 2027-11-01
GLCCD-EAGAN-SW14-VP-Column | Smart-UPS 1500 | WS1545180339 | v5.1.7 | 10.47.114.99 | RCCB Downey |  |  |  | 18.2
GLCCD-EAGAN-UPS-SW11-MRC | Smart-UPS 2200 | AS1648345196 | v7.1.2 | 10.20.207.96 | GLCCD Eagan |  |  |  | 19.39 | RBC43
GLCCD-EAGAN-UPS-SW12 | Smart-UPS 1500 | AS1742340870 | v6.5.0 | 10.20.206.15 | GLCCD Eagan |  |  |  | 29.48 | APCRBC133
GLCCD-EAGAN-UPS-SW16 | Smart-UPS 750 | AS1829144759 | v6.6.4 | 10.20.206.20 | GLCCD Eagan |  |  |  | 21.39 | RBC123
GLCCD-EAGAN-UPS-SW2 | Smart-UPS 2200 | AS2313152320 | v2.0.0.6 | 10.20.207.20 | GLCCD Eagan |  |  |  | 21.24 | RBC43 | 28.2 | 29.2 |  | 2027-10-17 | 2027-10-17
GLCCD-EAGAN-UPS-VP-Column | Smart-UPS 750 | AS1829144754 | v7.1.2 | 10.20.206.11 | GLCCD Eagan |  |  |  | 23.81 | RBC123
GLCCD-HighlandPark-UPS-MDF | Smart-UPS 3000 | AS2112162644 | v1.3.3.1 | 10.44.194.83 | GLCCD Highland Park |  |  |  | 29.23 | RBC43 |  |  |  | 2025-04-04 | 2025-08-18
GLCCD-Milwaukee-UPS-SW8-206 | Smart-UPS 3000 | AS2115271528 | v1.3.3.1 | 10.20.219.226 | GLCCD Milwaukee |  |  |  | 16.88 | RBC43 |  |  |  | 2027-08-30 | 2027-08-30
GLCCD-Niles-UPS-SW2-HQ2ndFl | Smart-UPS 1500 | AS1819341994 | v7.1.2 | 10.44.3.231 | GLCCD Niles |  |  |  | 19.82 | APCRBC133
GLCCD-Owatonna-UPS-MDF | Smart-UPS 3000 | AS1830340424 | v6.5.0 | 10.20.208.228 | GLCCD Owatonna |  |  |  | 26.2 | RBC43
GLCCD-ParkCity-UPS-DMARK | Smart-UPS 750 | 3S1723X02888 | v7.1.2 | 10.20.148.231 | GLCCD Park City |  |  |  | 27.3 | RBC48 | 5.9 | 5.9
GLCCD-StevensPoint-UPS | Smart-UPS 1500 | AS2112232306 | v1.3.3.1 | 10.20.222.131 | GLCCD Stevens Point |  |  |  | 17.17 | APCRBC133 | 17.51 | 18.2 |  | 2026-08-21 | 2026-08-21
GLCCD-Traverse-City-ups1 | Smart-UPS 1500 | 3S2221X13087 | v2.0.0.6 | 10.45.178.229 | GLCCD Traverse City |  |  |  | 25.46 | APCRBC133 | 24.8 | 25.8 |  | 2027-09-10 | 2027-11-01
MBUS-Dickson-MDF-UPS3 | Smart-UPS 1500 | AS2307153149 | v2.0.0.6 | 10.44.143.146 | MBUS Dickson |  |  |  | 21.8 | APCRBC133 |  |  |  | 2029-04-04 | 2029-04-04
MBUS-Fridley-MDF-UPS1 | Smart-UPS 2200 | AS2328132430 | v2.0.0.6 | 10.28.117.147 | MBUS Fridley |  |  |  | 21.4 | RBC43 | 25.91 | 27.3 |  | 2029-03-17 | 2029-03-17
MBUS-Fridley-MDF-UPS2 | Smart-UPS SRT 1500 | AS2234293821 | v2.0.0.6 | 10.28.116.23 | MBUS Fridley |  |  |  |  | APCRBC155 | 38.85 | 41.3
MBUS-Fridley-MDF-UPS3 | Smart-UPS SRT 1500 | AS2234293812 | v2.0.0.6 | 10.28.116.24 | MBUS Fridley |  |  |  |  | APCRBC155 | 0 | 0
MBUS-Lebanon-MDF-UPS1 | Smart-UPS SRT 1500 | AS2349392636 | v2.0.0.6 | 10.50.64.24 | MBUS Dickson |  |  |  |  | APCRBC155 | 47.86 | 49.9
MBUS-Lebanon-MDF-UPS2 | Smart-UPS SRT 1500 | AS2349392635 | v2.0.0.6 | 10.50.64.23 | MBUS Dickson |  |  |  |  | APCRBC155 | 0 | 0
MBUS-Manassas-IDF2-UPS | Smart-UPS 1500 | AS2307332119 | v2.0.0.6 | 10.50.250.59 | MBUS Manassas |  |  |  |  | APCRBC133 | 41.26 | 43.1
MBUS-MasonCity-MDF-UPS1 | Smart-UPS SRT 1500 | AS2234293820 | v2.0.0.6 | 10.53.80.23 | MBUS Mason City |  |  |  |  | APCRBC155 | 57.36 | 60.2
MBUS-MasonCity-MDF-UPS2 | Smart-UPS SRT 1500 | AS2234293809 | v2.0.0.6 | 10.53.80.24 | MBUS Mason City |  |  |  |  | APCRBC155 | 0 | 0
MBUS-Orlando-IDF1-UPS | Smart-UPS 1500 | AS2307154001 | v2.0.0.6 | 172.16.27.157 | MBUS Orlando |  |  |  | 8.31 | APCRBC133 |  |  |  | 2026-11-13 | 2026-11-13
MBUS-Orlando-RFIDTest1UPS | Smart-UPS X 1500 | AS2046142464 | v1.1.0.16 | 10.61.29.138 | MBUS Orlando |  |  |  | 7.16 | APCRBC115 |  |  |  | 2026-07-23 | 2026-07-23
MBUS-Stockton-MDF-UPS2 | Smart-UPS SRT 1500 | AS2129292956 | v1.3.3.1 | 172.16.24.162 | MBUS Stockton |  |  |  |  | APCRBC155 | 22.65 | 24.1
MBUS-Stockton-MDF-UPS3 | Smart-UPS SRT 1500 | AS2129292959 | v1.3.3.1 | 172.16.24.164 | MBUS Stockton |  |  |  |  | APCRBC155 | 20.13 | 20.6
RBD-San-Bernardino-UPS2 | Smart-UPS SRT 1500 | AS2111290794 | v1.3.3.1 | 10.28.60.24 | RBG San Bernardino |  |  |  | 26.16 | APCRBC155 |  |  |  | 2025-03-25 | 2025-05-22
RCCB-BISHOP-UPS | Smart-UPS X 3000 | AS1811153307 | v6.5.0 | 10.47.50.221 | RCCB Bishop |  |  |  | 20.91 | APCRBC117
RCCB-DOWNEY-UPS-s1p25 | Smart-UPS X 3000 | AS1804162955 | v6.5.0 | 10.47.115.228 | RCCB Downey |  |  |  | 20.81 | APCRBC143 | 7.94 | 13.8 |  | 2026-11-19 | 2026-12-09
RCCB-Fresno-UPS-SW2 | Smart-UPS X 1500 | AS1328226395 | v6.0.6 | 10.47.163.50 | RCCB Fresno |  |  |  | 20.28 | APCRBC115 |  |  |  | 2025-09-27 | 2025-09-27
RCCB-LAS-VEGAS-UPS2 | Smart-UPS X 3000 | AS1815360436 | v6.5.0 | 10.47.227.229 | RCCB Las Vegas |  |  |  | 24.01 | APCRBC117 | 38.59 | 40.1 |  | 2025-12-06 | 2025-12-07
RCCB-LOS-ANGELES-UPS-MDF-Rack2 | Smart-UPS X 3000 | AS1609263889 | v6.2.1 | 10.47.210.220 | RCCB Los Angeles |  |  |  | 20.5 | APCRBC117 | 19.37 | 24
RCCB-ParkCity-UPS-Cooler | Smart-UPS 1500 | AS2303165896 | v2.0.0.6 | 10.20.148.170 | GLCCD Park City |  |  |  | 25.18 | APCRBC133 |  |  |  | 2028-07-09 | 2028-09-23
RCCB-ParkCity-UPS-Driver | Smart-UPS 750 | AS2304230191 | v3.1.1.1 | 10.20.148.75 | GLCCD Park City |  |  |  | 28.42 | APCRBC123 | 53.94 | 55.8 |  | 2027-01-30 | 2028-02-10
RCCB-ParkCity-UPS-MDF | Smart-UPS 3000 | AS2223251267 | v2.0.0.6 | 10.20.148.139 | GLCCD Park City |  |  |  | 18.9 | RBC43 | 10.4 | 11 |  | 2027-09-06 | 2027-09-06
RCCB-Redding-UPS1 | Smart-UPS 2200 | C11918180289 | v5.1.7 | 10.48.98.228 | RCCB Redding |  |  |  | 16.33 |  |  |  |  | 2025-01-27 | 2025-01-27
RCCB-Sacramento-UPS2 | Smart-UPS 2200 | AS1820264202 | v6.5.0 | 10.47.178.229 | RCCB Sacramento |  |  |  | 30 | RBC43
Unknown | Smart-UPS X 3000 | AS1303145957 | v5.1.7 | 10.20.33.214 | RBG Chesapeake-VA |  |  |  | 22.39 |  |  |  |  | 2026-12-24 | 2026-12-24
Unknown | Smart-UPS X 3000 | JS1113002683 | v5.1.7 | 10.20.33.208 | RBG Chesapeake-VA |  |  |  | 22.85 |  |  |  |  | 2028-05-13 | 2028-05-13
apc04A4AE | Smart-UPS 1500 | AS1808134114 | v6.5.0 | 10.51.128.97 | RBG West Sacramento |  |  |  | 18.09 | RBC7
apc12AE3E | Smart-UPS 1500 | AS1832234457 | v7.1.2 | 10.20.33.216 | RBG Chesapeake-VA |  |  |  | 19.56 | APCRBC133
apc223F8E | Smart-UPS 750 | AS1920330006 | v7.1.2 | 10.20.33.215 | RBG Chesapeake-VA |  |  |  | 28.86 | RBC123
apc32C548 | Smart-UPS 750 | AS2010133195 | v6.8.2 | 10.52.26.192 | RBG Indianapolis |  |  |  | 17.97 | RBC123
apc32D413 | Smart-UPS 750 | AS2010133193 | v6.8.2 | 10.52.26.94 | RBG Indianapolis |  |  |  | 18.82 | RBC123
apc32E9A4 | Smart-UPS 750 | AS2010133157 | v6.8.2 | 10.52.26.249 | RBG Indianapolis |  |  |  | 18.07 | RBC123
apc32E9CD | Smart-UPS 750 | AS2010133146 | v6.8.2 | 10.52.26.191 | RBG Indianapolis |  |  |  | 32.42 | RBC123
apc32E9D7 | Smart-UPS 750 | AS2010133147 | v6.8.2 | 10.52.27.164 | RBG Indianapolis |  |  |  | 15.71 | RBC123
apc3E2734 | Smart-UPS 750 | AS2033142979 | v7.1.2 | 10.20.38.117 | RBG Pompano |  |  |  | 25.01 | RBC123 |  |  |  | 2026-03-19 | 2026-03-29
apc64CD5B | Smart-UPS SRT 1500 | AS2126291548 | v1.5.1.1 | 10.54.27.118 | RBG Orion |  |  |  | 20.94 | APCRBC155 |  |  |  | 2027-02-12 | 2027-02-12
apc853F9E | Smart-UPS 2200 | AS1430142077 | v6.0.6 | 172.16.67.96 | RBG San Bernardino |  |  |  | 27.84 | RBC43
apcB60E3A | Smart-UPS 2200 | AS1346243781 | v7.1.2 | 192.168.50.116 | MBCAN Vancouver |  |  |  | 24.22 | RBC43 |  |  |  | 2028-02-15 | 2028-02-28
apcB60EBC | Smart-UPS 2200 | AS1351140727 | v6.0.6 | 192.168.50.110 | MBCAN Vancouver |  |  |  | 22.98 | RBC43 |  |  |  | 2026-10-11 | 2026-10-11
apcB6D5C5 | Smart-UPS 2200 | AS1348244025 | v6.0.6 | 192.168.60.152 | MBCAN Moncton |  |  |  | 19.31 | RBC43 |  |  |  | 2028-04-15 | 2028-04-15
apcB6D7AD | Smart-UPS 2200 | AS1346243780 | v6.0.6 | 192.168.40.127 | MBCAN Montreal |  |  |  | 19.78 | RBC43
apcB6D7BD | Smart-UPS 2200 | AS1348244026 | v6.0.6 | 192.168.60.159 | MBCAN Moncton |  |  |  | 19.56 | RBC43
apcB6D7C9 | Smart-UPS 2200 | AS1346243707 | v6.0.6 | 192.168.80.159 | MBCAN Winniepeg |  |  |  | 21.76 | RBC43 |  |  |  | 2027-06-29 | 2027-06-29
apcF3601F | Smart-UPS 2200 | AS1430141971 | v7.1.2 | 10.45.18.53 | RBG Frederick |  |  |  | 29.99 | RBC43 | 5.07 | 6 |  | 2026-03-15 | 2027-03-02
apcF510A1 | Smart-UPS 1500 | 3S1621X00080 | v7.1.2 | 10.45.18.51 | RBG Frederick |  |  |  | 30.32 | RBC7 | 22.79 | 23.4